## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
1BR-BA | 1 Bed Room - Bariatric | 18 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Bariatric will accommodate one patient, typically weighing up to 250kg, for the delivery of a range of clinical care and treatment. The spatial allowance will accommodate: staff working at either side of the bed, however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door - the arrangement of the medical services panel reflects this assumption; bariatric sized equipment (bed, chair) and the movement of equipment around all sides of the bed; a ceiling mounted hoist that extends from the bed to the Ensuite. Natural light and outlook is essential and patients will need to have an external outlook from either the chair or the bed, preferably both. The 1 Bed Room may also be used as an Isolation Room - Class S (Standard Pressure). Door glazing is recommended. This room should be planned with direct access to an Ensuite - Bariatric. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.

## Items in room
Standard Components - Items in room
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-BA | 1 Bed Room - Bariatric | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | DWGL-076 | DOOR: 1600mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | DWWD-001 | BLIND: blackout | 1 | provide additional anti glare blinds where required | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELBO-015 | SWITCH: light, single | 3 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-109 | GPO: single, wall mounted | 1 | for patient entertainment display screen | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-109 | GPO: single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ELPR-006 | RCD: residual current device | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P2 (prefer P3) to extend under basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FQGE-010 | CURTAIN: privacy screen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 | display screen size to suit wall mounted location | Yes | Yes | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 |  | No | Yes | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replaced with data outlet, decision to be made at project level | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-004 | BED: patient, bariatric, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-053 | LIFTER: patient, ceiling mounted, cassette motor for track, bariatric | 1 | for patient lifter track | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-055 | LIFTER: patient, ceiling mounted, sling component, bariatric | 1 | for patient lifter motor | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMBE-061 | LIFTER: patient, ceiling mounted, track, traverse, bariatric | 1 | to connect to ensuite lifter | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-002 | ADAPTER: suction | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-020 | CHAIR: patient, bariatric | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No