## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | 16.5 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors |  | Acoustic privacy is required | A 1 Bed Room - Isolation (Negative Pressure) will accommodate one patient requiring respiratory isolation to prevent the transmittion of infection. The room will be capable of delivering a range of clinical care and treatment. The room will have an attached Anteroom which will be used by staff and visitors so they can don PPE. The patients will be transferred in and out of the room via the patient doors, rather than the Anteroom. This arrangement also makes the room easier to use when not needed for negative pressure isolation. The spatial allowance will accommodate: staff working at either side of the bed however it is assumed that nursing care will predominately occur at the side of the bed closest to the entry door. The arrangement of the medical services panel reflects this assumption the movement of equipment around all sides of the bed (e.g. a mobile hoist) a ceiling mounted hoist. While this item is shown, inclusion will be dependent on jurisdictional policies. Natural light and outlook is essential and the patients will requirement outlook from either the bed or chair, preferably both. Door glazing and an internal window is recommended with this option but will depend on the location of the Ensuite. For further information relating to specific requirements, refer to AusHFG Isolation Rooms - Engineering and Design Requirements. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project.

## Items in room
Standard Components - Items in room
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiles may also be acceptable dependent upon acuity of patient | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | joinery can optionally be used as bulkhead above cupboard | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | door closer required. Obs panel could alternatively be provided in wall | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 4 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to window | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to optional observation panel, if provided | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | DWWH-005 | WINDOW | 1 | natural light & outlook essential | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELBO-015 | SWITCH: light, single | 4 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-105 | GPO: single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-109 | GPO: single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ELPR-006 | RCD: residual current device | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-022 | DISPENSER: moisturiser | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FIRT-040 | TRACK: curtain, privacy, L shaped, angled | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin; sensor mixer optional | No | No | Yes | No | Yes | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, + light switch on the handset | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel, 1 outlet for telephone | No | Yes | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | ITIN-070 | OUTLET: MATV | 1 | for patient entertainment system. May be replace with data outlet, decision to be made at project level | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MEEX-008 | EXHAUST: low level | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-052 | LIFTER: patient, ceiling mounted, cassette motor for track | 1 | optional, for patient lifter track | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-054 | LIFTER: patient, ceiling mounted, sling component | 1 | optional, for patient lifter motor | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMBE-056 | LIFTER: patient, ceiling mounted, track, linear | 1 | optional, consideration of sealing of ceiling fixing requried | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-019 | CHAIR: patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No