## Room data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | 15 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors | Acoustic privacy is required | Single bed room for general mental health patients. Natural light and outlook is essential. The room is to be internally lockable with a master keyed lock from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. clothes hooks). All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. The 1 Bed Room - Mental Health may vary in configuration to suit different Ensuite options, including inboard and back to back. Staff to staff nurse call has not been provided on the assumption that a portable call and duress device is provided to staff. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | DWGL-074 | DOOR: 1120mm c/o, 1 1/2 leaf in/out opening, observation panel, solid core/safety glass, paint | 1 | lockable, anti ligature door hardware | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to window/s, obs panel in door | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | DWWH-005 | WINDOW | 1 | natural light and outlook essential | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELBO-015 | SWITCH: light, single | 3 | plus two located outside door for light and night light; lighting to have controlled switching to create low stimulus environment. one may optionally be replaced with light motion sensor deactivation switch | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-109 | GPO: single, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | to desk | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIBM-015 | NOTICEBOARD: fixed, velcro | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional, glued to backing material and screw fixed | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-210 | BEDHEAD: mental health | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FIJO-215 | CUPBOARD: tall, shelf unit, fixed shelves, anti-ligature, 500D | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQBS-054 | STOOL: ottoman | 1 | suitable for mental health environments | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQBS-056 | CHAIR: tub, mental health | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQDW-025 | DESK: built in, return end, anti ligature | 1 | laminate finish | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQSN-062 | SAFE: small | 1 | optional, for patient belongings, suitable for mental health environments, bolt into place | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | FQTA-083 | TABLE: bedside, anti ligature | 1 | unit is weighted, optional choice of tamper proof wheels or sliders for mobility. Fixed unit is optional alternative | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional depending on client age group and jurisdicational policy; mobile duress preferred; + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | ITSE-047 | SENSOR: motion detection, for staff alert, flush to ceiling | 1 |  | Yes | Yes | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | LIFX-001 | LIGHT: night light, tamper proof, anti ligature | 1 | recommended to be on emergency power | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1 | can also be wall recessed | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FFE | MMBE-017 | BED: patient, mental health, electric | 1 | or mattress on built-in plinth | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLWA-003 | WALL FINISH: laminated composite board | 1 | to back of ensuite door | No | No | No | No | No | No | No | No | No
1BR-MH-A | 1 Bed Room - Mental Health - Inboard Ensuite, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No