## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | 15 | 24 Hours | 1 patient; 1-2 staff; 1-2 visitors | Acoustic privacy is required | Single bed room for general mental health patients. Natural light and outlook is essential. The room is to be internally lockable with a master keyed lock from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. clothes hooks). All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. The 1 Bed Room - Mental Health may vary in configuration to suit different Ensuite options, including inboard and back to back. Staff to staff nurse call has not been provided on the assumption that a portable call and duress device is provided to staff. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.

## Items in Room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWGL-074 | DOOR: 1120mm c/o, 1 1/2 leaf in/out opening, observation panel, solid core/safety glass, paint | 1 | lockable, anti ligature door hardware, obs panel can be omitted if obs window provided | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | optional, dependent on jurisdicational policy and acuity level of unit. control to patient side | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 2 | to window/s and obs panel in door | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | optional, to optional obs panel in wall | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | DWWH-005 | WINDOW | 1 | natural light and outlook essential | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELBO-015 | SWITCH: light, single | 3 | Plus two additional located outside door for light and night light. Lighting to have controlled switching to create low stimulus environment. one may optionally be replaced with light motion sensor deactivation switch | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-109 | GPO: single, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | optional | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | to desk | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIBM-015 | NOTICEBOARD: fixed, velcro | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional, glued to backing material and screw fixed | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-134 | CUPBOARD: tall, shelf unit, fixed shelves, anti-ligature, 600D | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-210 | BEDHEAD: mental health | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FIJO-212 | BULKHEAD: joinery | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQBS-054 | STOOL: ottoman | 1 | suitable for mental health environments | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQBS-056 | CHAIR: tub, mental health | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQDW-025 | DESK: built in, return end, anti ligature | 1 | laminate finish | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQSN-062 | SAFE: small | 1 | optional, for patient belongings, suitable for mental health environments, bolt into place | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | FQTA-083 | TABLE: bedside, anti ligature | 1 | unit is weighted, optional choice of tamper proof wheels or sliders for mobility. Fixed unit is optional alternative | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | optional depending on client age group and jurisdicational policy; mobile duress preferred; + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | ITSE-047 | SENSOR: motion detection, for staff alert, flush to ceiling | 1 |  | Yes | Yes | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | LIFX-001 | LIGHT: night light, tamper proof, anti ligature | 1 | recommended to be on emergency power | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1 | can also be wall recessed | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FFE | MMBE-017 | BED: patient, mental health, electric | 1 | or mattress on built-in plinth | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLWA-003 | WALL FINISH: laminated composite board | 1 | for wall protection behind ensuite door | No | No | No | No | No | No | No | No | No
1BR-MH-C | 1 Bed Room - Mental Health - Back to Back Ensuites, 15m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No