## RDS
Standard Components - Room Data Sheet
Date of issue: 22.06.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
1BR-SP-B | 1 Bed Room - CCU, 20m2 | 20 | 24 Hours | 1 patient; 1-2 visitors, 1-2 staff intermittently |  | Acoustic privacy is required | A 1 Bed Room - Special, Coronary Care will accommodate one patient for the delivery of cardiac care treatment. Glazed doors and partition walls are recommended for patient visibility and privacy. Natural light and outlook is essential; the room requires the ability to view out of the window from either the chair or bed.

## Items in room
Standard Components - Items in room
Date of issue: 22.06.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | latch set with hold open device; observation panel optional. | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | to internal observation window | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | DWWD-011 | CURTAIN: window, drapes | 1 | set | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | DWWH-005 | WINDOW | 1 | Natural light & outlook essential. | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELBO-015 | SWITCH: light, single | 4 | on service panel (1 no,) | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | adjacent to patient chair | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-109 | GPO: single, wall mounted | 1 | bedhead low level, for electric bed | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ELGP-206 | GPO: double, on services panel, RCD protected | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | near basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIHR-013 | BRACKET: for monitor, ECG | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 2 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIJO-193 | SHELF: flowers | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIRT-021 | TRACK: curtain, bedscreen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FIRT-027 | TRACK: curtain, box pelmet | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | FLVY-006 | FLOOR FINISH: vinyl, seamless, coved, non slip, textured | 1 | under basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FQGE-009 | CURTAIN: bed screen | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 |  | No | No | Yes | No | Yes | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel, + indicator button & light | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light+ indicator button & light | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light+ indicator button & light | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, with light switch | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 | optional, for monitor communications with associated cabling and connections; verify outlet type/s with monitor selected | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | ITIN-070 | OUTLET: MATV | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | LIFX-011 | LIGHT: reading light | 1 | up/down light | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MMGE-019 | CHAIR: patient | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FFE | MMHA-005 | MONITOR: patient, cardiac | 1 | may be telemetry | Yes | Yes | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | WLPR-012 | WALL PROTECTION: corner guards, to 900 AFFL, prefinished PVC | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No