## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ADLB | ADL Bathroom | 12 | 24 Hours | 1 patient; 1 - 2 staff assisting |  | Sound attenuation level medium, Acoustic privacy is required. | A bathroom for patient 'Activities of Daily Living' assessment and training. The ADL Bathroom provides for training of patients to use a domestic bath and shower, patient dressing, undressing, grooming and handwashing. Facilities include a domestic bath installed in a corner of the room, toilet and handbasin and a separate shower within the room. A low height adjustable shower is required over the bath. Additional Design Requirements: - The shower area must not have a raised, fixed hob. - The entrance to the bathroom is to be flush with the adjoining corridor. - The door is to be fitted with escape hardware.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ADLB | ADL Bathroom | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | Water resistant flush set suspended ceiling is also acceptable | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional - to be decided at project level | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 | privacy latch | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | above basin | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIBM-007 | MIRROR: fixed, glass, full length | 1 | dressing | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin, optional for shower and bath areas. | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | on hinged grab rail | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 2 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1000H | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIJO-191 | SHELF: above basin | 1 | or integrated with basin | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 | combined with hand held shower | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 2 | drop down rails both sides of WC; 1 x toilet paper dispenser, 1 x NC | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail fixings | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 | optional, depends on infection control policy | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | significant change in colour from adjacent corridor to be avoided; suitable for barefeet. | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FQBS-008 | BENCH SEAT: freestanding, patient transfer | 1 | portable - not fixed, near bath | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FQCW-037 | BIN: waste, sanitary | 1 | optional, depends on waste management policy | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, depends on infection control policy. | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 | with integral shelf for patient belongings or separate shelf | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FFE | HYBA-025 | BATH: domestic | 1 | warm water; agree tapware on project basis | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | SE | HYDR-004 | DRAIN: floor waste | 2 |  | No | No | No | No | No | No | Yes | No | No
ADLB | ADL Bathroom | FFE | HYTP-020 | SHOWER: hand-held | 1 | to shower | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FFE | HYTP-021 | SHOWER: hand-held, over bath | 1 | optional; low level over bath | No | No | Yes | No | Yes | Yes | Yes | No | No
ADLB | ADL Bathroom | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ADLB | ADL Bathroom | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 | short lever taps | No | No | Yes | No | Yes | No | No | No | No
ADLB | ADL Bathroom | FFE | HYWC-006 | TOILET SUITE: patient | 1 |  | No | No | Yes | No | No | Yes | Yes | No | No
ADLB | ADL Bathroom | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 3 | + indicator button & light | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FFE | MMGE-024 | CHAIR: shower | 1 | or commode chair or combined shower/commode chair. | No | No | No | No | No | No | No | No | No
ADLB | ADL Bathroom | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to shower area, tiles also acceptable | No | No | No | No | No | No | No | No | No