## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
AUDIO | Audiology Testing Room | 14 | 8am to 6pm, daily | Up to 3 |  | Acoustic privacy is required | Room with an internal sound proof booth to specifications, for audiology testing. Audiometric booth should be ventilated or connected to air-conditioning, power and data. Level access to the Audiometric Booth is recommended.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
AUDIO | Audiology Testing Room | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ELBO-015 | SWITCH: light, single | 3 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ELGP-106 | GPO: single, special, for equipment | 1 | audiometric booth | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ELGP-208 | GPO: double, wall mounted | 4 | 2- desk; 2-booth | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FIBM-018 | WHITEBOARD: fixed | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FIHR-026 | HOOK: coat | 2 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | FLCP-003 | FLOOR FINISH: carpet, broadloom, 48 oz., 90/10 wool/nylon | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQBS-012 | CHAIR: child | 1 | as required | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQBS-014 | CHAIR: client | 3 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQDW-002 | DESK: adj height, 1800W x 750D x 750H nom. | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 1 | under desk | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | FQTA-032 | TABLE: rectangular, 850L x 550W, work height | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | FSDE-004 | DETECTOR: smoke | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | 1 to booth, 1 outlet to desk for telephone | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 |  | Yes | Yes | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | on desk | No | Yes | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 |  | No | No | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | MMAH-005 | BOOTH: audiometric | 1 | to specification | Yes | Yes | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FFE | MMAH-036 | CONSOLE: control, audiometric booth | 1 |  | Yes | Yes | No | No | No | No | No | No | No
AUDIO | Audiology Testing Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No