## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BBW | Bay - Blanket/ Fluid Warmer | 1 | 24 Hours |  |  |  | A Bay for a blanket or combined blanket / fluid warming cabinet. The bay should have close access to patient areas and operating rooms. Assess dimensions of cabinet to ensure space is adequate. When blanket warming is accommodated, ideally located near a Linen Bay.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
BBW | Bay - Blanket/ Fluid Warmer | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | Acoustic tiles acceptable. | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FFE | MMGE-010 | CABINET: blanket/ fluid warming | 1 | Freestanding | Yes | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 1 | Align heights of corner guards with other corridor elements | No | No | No | No | No | No | No | No | No
BBW | Bay - Blanket/ Fluid Warmer | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No