## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BIRM-B | Birthing Room - LDR With Bath | 40.5 | 24 Hours | 1 mother; 1-2 support persons; up to 4 staff |  | Sound attenuation level high, Acoustic privacy is required. | The Birthing Room LDR (with birthing bath/ pool) provides for the entire process of delivery including mother's preparation, relaxation and analgesia during labour, delivery, infant resuscitation, post natal recovery and observation. The Birthing Room will include a scrub basin. Clinical items such as medical gases and services may be concealed but within easy reach. The room will have direct access to an Ensuite - Birthing. The room can be used for an extended stay where LDPR models are used. The birth bath/ pool is routinely used for water immersion during labour. It may also be used for water births but this will need to be supported by local policies. A ceiling mounted hoist has not been included as there are better and more timely ways to remove a mother from the bath should her condition deteriorate. Refer to HPU510 Maternity Unit for details. Note that the overall room area includes a 2m2 Equipment Store. Notes applied to floor ratings respond to current AS 4586 and associated HB198 requirements - compliance with current regulations and jurisdictional policy must be verified by project teams on each project. Negative pressure air conditioning is required for clearance of anaesthetic gases.

## Items in room
Standard Components - Items in room
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
BIRM-B | Birthing Room - LDR With Bath | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 2 | above joinery items, joinery bulkhead can alternatively be provided | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 3 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 | with latchset and hold open device | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | DWWD-011 | CURTAIN: window, drapes | 1 | set | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | DWWH-005 | WINDOW | 2 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELBO-015 | SWITCH: light, single | 4 | to ensuite, wall panel, door, store | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | for ceiling mounted display screen (TV) | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-109 | GPO: single, wall mounted | 4 | patient side | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 4 | staff side | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-205 | GPO: double, on services panel | 2 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-208 | GPO: double, wall mounted | 1 | low level, for electric bed | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELGP-208 | GPO: double, wall mounted | 3 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ELPR-006 | RCD: residual current device | 4 | 1 to staff side, 1 to patient side, 2 to infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | to infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | to basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIHR-016 | BRACKET: for sharps bin | 1 | mounted to trolley | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIJO-130 | CUPBOARD: tall, single door, adj shelves and clothes rail | 1 | wardrobe | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIJO-160 | CUPBOARD: wall mount, double door, fixed shelf over | 1 | for towels | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIJO-162 | CUPBOARD: tall, single door, to conceal services | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIRT-030 | TRACK: curtain, flat pelmet | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1 | to door entry | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | to bath area | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQBS-001 | BASSINET | 1 | optional, if used for post-natal care | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1 | to bench | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQBS-041 | LOUNGE: 2.5 seat | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQBS-051 | STOOL: mobile, adj height | 1 | for partner of birthing mother when at bath | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQCW-043 | BIN: waste, sharps, on trolley | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQDW-039 | DESK: adj height, 800W x 600D x 1000H nom. | 1 | recommended adjustable range 900-1100mm high | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to door to room | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | optional, to door to equipment store | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQSM-016 | TROLLEY | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQSN-051 | LOCKER: 2 drawers, open under, lockable, mobile | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQTA-013 | TABLE: overbed | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | FQTA-053 | TABLE: round, 600 diam, low height | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 | refer to BWHS-A (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | HYBA-023 | BATH: birthing | 1 | integral water and drainage | No | No | Yes | No | Yes | Yes | Yes | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 |  | No | No | Yes | No | Yes | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITCL-004 | BUTTON: nurse call, emergency | 2 | staff side and at infant resus, + indicator button & light | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | patient side, + indicator button & light | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | staff side and to bath, + indicator button & light | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | patient side, with light switch | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | above bench, 1 outlet for telephone | No | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | patient side | No | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | ITIN-070 | OUTLET: MATV | 1 | may be replaced with data outlet depending on entertainment system | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 |  | Yes | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 |  | No | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | LIFX-011 | LIGHT: reading light | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | LIFX-017 | LIGHT: night light | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | optional | Yes | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | LIPO-006 | LIGHT: examination, mobile | 1 |  | Yes | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-023 | OUTLET: medical air (MA), wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 2 | in cupboard, to bath | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 3 | in cupboard (2), to bath (1) | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-055 | OUTLET: scavenge, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-063 | OUTLET: suction, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MGFP-002 | FLOWMETER: medical air | 2 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MGFP-004 | FLOWMETER: oxygen | 4 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMBE-005 | BED: patient, birthing, electric | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMGE-063 | MONITOR: patient, foetal, CTG | 1 | mobile | Yes | Yes | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMMA-011 | MIXER: oxygen and nitrous oxide | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMMA-016 | RESUSCITAIRE: infant, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FFE | MMMA-017 | MANTLEPIECE: birthing, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | to infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 5 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin | No | No | No | No | No | No | No | No | No