## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BLST | Blood Store | 2 | 24 Hours |  |  |  | The Blood Store is a bay for refrigerated storage of blood and blood products. The Bay will be located with ready access to Operating Rooms and patient treatment areas.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
BLST | Blood Store | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
BLST | Blood Store | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
BLST | Blood Store | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
BLST | Blood Store | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
BLST | Blood Store | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
BLST | Blood Store | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2 | for temperature monitor/alarms, optional | No | No | No | No | No | No | No | No | No
BLST | Blood Store | FFE | MMLA-053 | FRIDGE: blood products, single door | 3 | with temperature monitor | Yes | Yes | No | No | No | No | No | No | No
BLST | Blood Store | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 | Equal to 'Acrovyn' | No | No | No | No | No | No | No | No | No
BLST | Blood Store | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No