## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
BMT-4 | Bay - Meal Trolley, 4m2 | 4 | 24 Hours |  |  |  | An open storage bay for holding meal trolleys during meal delivery and collection times. Meal service and mid-meal trolleys to be confirmed; special power may be required for Cook/chill rethermalisation trolleys. Special Design Requirements: The Bay should be deep enough to ensure trolleys do not impede corridor circulation; minimum depth 1200mm, however, the depth may need to increase to 1500mm depending on the trolley selected.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
BMT-4 | Bay - Meal Trolley, 4m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | Acoustic tiles acceptable. | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | SE | ELGP-240 | GPO: three phase, double | 1 | 1 per food delivery or rethermalisation trolley, as required | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | Default = vinyl: or consistent with adjacent area | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Default = vinyl: or consistent with adjacent area | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FFE | FQCA-082 | TROLLEY: food delivery, hot/cold | 1 | as required | Yes | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FFE | FQSM-037 | TROLLEY: tray | 1 | as required, depends on food delivery system | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | WLPR-010 | WALL PROTECTION: corner guards, to 900 AFFL | 1 | Align heights of corner guards with other corridor elements | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | WLPR-021 | WALL PROTECTION: crash rail, at 900 AFFL | 1 | As required. | No | No | No | No | No | No | No | No | No
BMT-4 | Bay - Meal Trolley, 4m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No