## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
COMM | Communications Room | 12 | 24 Hours | 1 - 2 intermittently |  |  | A secure room for engineering services to accommodate communications racks, interface control panels for communication systems which may include MATV, Nurse Call and Fire/EWIS system and voice/data backbone cabling. Equipment located in this room will require uninterruptible power which should be fed from the essential supply (generator). It may also need air conditioning depending on heat load. Area shown is indicative only. The size of the Communications Room will be project specific and will vary according to engineering consultant advice. The Communication Room must be located such that it is not susceptible to possible water damage or excessive electromagnetic interference. Water or gas pipes must not pass through a Communication Room.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
COMM | Communications Room | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | Lockable | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | DWPR-003 | DOOR PROTECTION: kickplate, to 300 AFFL, vinyl, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Optional, to be decided at project level | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ELBO-004 | DISTRIBUTION BOARD | 1 | UPS, single phase | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ELGP-106 | GPO: single, special, for equipment | 7 | As required. Refer project specific requirements. | No | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ELGP-208 | GPO: double, wall mounted | 9 | As required. Refer project specific requirements. | No | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ELGT-007 | UPS: uninterruptable power supply unit | 1 | as required | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | FIJO-044 | BENCH: special depth, open under | 1 | Optional, 700D, laminate finish, length to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | FLVY-001 | FLOOR FINISH: vinyl, seamless, coved, anti-static | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 | optional | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | FSDE-008 | CONTROL PANEL: fire and EWIS | 1 | optional | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | Number depends on equipment. Refer project specific requirements. | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITIN-123 | RACK: communications | 1 | As required. Refer project specific requirements. | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITIN-128 | RACK: voice, intermediate distribution frame (IDF) | 1 | Optional. Refer project specific requirements. | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITIN-139 | COMPUTER: mainframe | 1 | As required. Refer project specific requirements.. | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITNE-005 | COMMS BOARD | 1 | As required. Refer project specific requirements. | Yes | No | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 2 | Flat screen, as required. Refer project specific requirements. | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITNE-011 | COMPUTER: server | 1 | As required. Refer project specific requirements. | Yes | Yes | No | No | No | No | No | No | No
COMM | Communications Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
COMM | Communications Room | SE | ITSE-038 | READER: access control, general | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | SE | ITSE-046 | SENSOR: motion detection, for staff alert | 1 |  | No | No | No | No | No | No | No | No | No
COMM | Communications Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No