## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
CONS | Consult Room | 12 | 24 Hours | 1 patient: 1-2 staff, 1-2 visitors | For bariatric consult requirements refer toTreatment Room options | Sound attenuation level high, Acoustic privacy is essential. | The Consult Room will provide for private consultation and physical examination of patients with or without support persons present. A second egress door may be required for staff safety and security and/or staff access. A hoist, fixed or ceiling mounted (depending on local arrangments) may be required for selected clinical situations.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
CONS | Consult Room | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | CLGE-001 | CEILING: plasterboard, bulkhead, paint | 1 | Between above bench joinery and ceiling | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 | Min. 1350mm clear opening with 910 large leaf, or a 1200mm clear opening single door. Bariatric provision to be decided at project level | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2 | Optional, to be decided at project level | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-105 | GPO: single, on services panel | 1 | diagnostic set | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | low level for electric couch | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | Above bench for BYO device | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | for exam light | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-205 | GPO: double, on services panel | 1 | patient examination area | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-208 | GPO: double, wall mounted | 2 | workstation / desk area | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ELGP-222 | GPO: emergency power, double, on services panel | 1 | patient examination area | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | for patient changing | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 1 | over desk, optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-003 | DISPENSER: bedroll | 1 | Or provided as an attachment to exam couch | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-022 | DISPENSER: moisturiser | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to hand basin | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIHR-026 | HOOK: coat | 2 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 1 | over desk, optional, number to suit layout refer to RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FIRT-023 | TRACK: curtain, bedscreen, L shaped | 1 | to exam couch | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5 | Feather edge vinyl skirting if carpeted | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Carpet also acceptable | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | Under basin, significant colour change to be avoided | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 3 | Consider weight capacity of chair | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | Wall mounted | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQDW-001 | DESK: adj height, 1100W x 600D x 750H nom. | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | FQGE-009 | CURTAIN: bed screen | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | elbow action levers | No | No | Yes | No | Yes | Yes | Yes | No | No
CONS | Consult Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
CONS | Consult Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | High resolution monitor for PACS viewing | Yes | Yes | No | No | No | No | No | No | No
CONS | Consult Room | FFE | ITNE-023 | PRINTER: networked | 0 | EMR/E-med compatible, printing strategy (centralised vs decentral) to be decided at project level | Yes | Yes | No | No | No | No | No | No | No
CONS | Consult Room | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1 |  | No | Yes | No | No | No | No | No | No | No
CONS | Consult Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1 | Default= wall mounted: or ceiling mounted | Yes | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMBE-023 | COUCH: examination, electric, mobile | 1 | Hi / low operation | Yes | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMGE-002 | ADAPTER: suction | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1 |  | Yes | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMGE-091 | SPHYGMOMANOMETER: portable | 0 | 1 per 6 Consult Rooms. Ratio to be determined at project level. | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMGE-100 | SUCTION BOTTLE | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FFE | MMGE-153 | VIEWER: X-ray, 2 screen, mobile | 0 | 1 per department, number and location to be decided at project level | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
CONS | Consult Room | FA | WLWA-007 | WALL FINISH: splashback | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG | No | No | No | No | No | No | No | No | No