## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DENSR-16 | Dental Surgery, 16m2 | 16 | Available 24 Hours | 1 patient, 1-2 staff; 1 support person as required |  | Sound attenuation level high, Acoustic privacy is required. | The Dental Surgery provides for dental consultation, examination and treatment for patients. An external outlook is desirable. The 16m2 room provides for access by patient trolleys as required. Additional Design Considerations: Radiation shielding to be advised by Radiation Consultant. Services will be required for the dental chair unit which will be dependant on the chair model and supplier and will include dental air, dental suction, filtered water, power and drainage.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DENSR-16 | Dental Surgery, 16m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | DWGL-024 | DOOR: 1200mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | DWWD-006 | BLIND: venetian | 1 | to external windows, if provided | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | DWWH-005 | WINDOW | 1 | desirable | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELGP-107 | GPO: single, special, for equipment, floor mounted | 1 | Dental Chair & services unit | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELGP-109 | GPO: single, wall mounted | 2 | XR Viewer & XRay Unit | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELGP-208 | GPO: double, wall mounted | 8 | 2 for workstation area | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIBM-018 | WHITEBOARD: fixed | 1 | 500x500 (optional) | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIDI-021 | DISPENSER: mask | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to vanity basin | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to vanity basin | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to vanity basin | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIHR-031 | HOOK: heavy duty | 2 | for lead aprons; may also use wall mounted hanging rail | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIJO-102 | CUPBOARD: drawer unit | 1 | under bench, with slide out tray | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 2 | under work bench | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIJO-145 | CUPBOARD: wall mount, double door, adj shelves, lockable | 3 | over bench | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIJO-157 | CUPBOARD: wall mount, single door, adj shelves, lockable | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FIJO-203 | BENCH TOP: 600D, joinery under, laminate finish, corner unit | 1 | with inset basin & sink, to 2 sides, open uner part for workstation and underbench mobile units | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FQBS-051 | STOOL: mobile, adj height | 2 | 1 high ergonomic stool for 900H workstation bench | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | under bench | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | HYBA-013 | BASIN: vanity | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | HYBA-051 | SINK: single | 1 | warm water | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 2 | 1 to basin, 1 to sink | No | No | Yes | No | Yes | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 1 | flat screen | Yes | Yes | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | to bench | No | Yes | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | wall mounted (optional) | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | LIFX-008 | LIGHT: task light, built in | 1 | under O/H cupboards | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMBE-062 | LIFTER: patient, ceiling mounted, track, U shape | 1 | optional | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMDN-002 | CHAIR: dental, electric | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMDN-015 | SERVICE UNIT: dental, chair (spitoon) | 1 | includes intrument tray, light & spitoon; spitoon is optional, depending on operational policy | Yes | No | Yes | No | No | No | Yes | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMDN-016 | TROLLEY: dental | 1 | under bench; dental instruments and supplies | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMDN-018 | X-RAY UNIT: dental, wall mounted | 1 |  | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMDN-019 | LIGHT: dental | 1 | part of chair service unit | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMGE-002 | ADAPTER: suction | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | MMGE-150 | VIEWER: X-ray, 1 screen | 1 |  | Yes | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FFE | WLPT-003 | PARTITION: laminate | 1 | under bench | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 |  | No | No | No | No | No | No | No | No | No