## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DENW | Dental Workroom | 12 | 8am to 6 pm daily | 1 - 2 |  | Sound attenuation high: Acoustic privacy required | The Dental Workroom provides facilities and equipment for dental technicians to make adjustments to dentures or other dental prosthetics, and to store prosthetic supplies.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DENW | Dental Workroom | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | ELGP-208 | GPO: double, wall mounted | 4 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIDI-021 | DISPENSER: mask | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 2 | with wet edge, open under part, one leg 650D | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 4 | over bench | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FIJO-197 | SHELF: stainless steel, underbench | 4 | under bench | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
DENW | Dental Workroom | FFE | HYBA-069 | SINK: single, with drainer, 930mmL | 1 |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DENW | Dental Workroom | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
DENW | Dental Workroom | FFE | HYDR-008 | TRAP: plaster | 1 | under sink | No | No | No | No | No | No | Yes | No | No
DENW | Dental Workroom | SE | HYTP-008 | OUTLET: cold water | 1 | additional outlet for equipment | No | No | Yes | No | No | No | No | No | No
DENW | Dental Workroom | SE | HYTP-014 | OUTLET: natural gas | 1 | for bunsen burner | No | No | No | No | No | No | No | Yes | No
DENW | Dental Workroom | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to sink | No | No | Yes | No | Yes | No | No | No | No
DENW | Dental Workroom | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
DENW | Dental Workroom | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 | optional | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | LIFX-008 | LIGHT: task light, built in | 4 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | MEEX-007 | EXHAUST: hood | 1 | over dental processing equipment | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | MGAS-008 | OUTLET: compressed air, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | MMDN-008 | GRINDER: dental, workshop | 1 |  | Yes | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | MMDN-009 | LATHE: dental, polishing | 1 |  | Yes | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FFE | MMDN-017 | UNIT: processing, denture | 1 |  | Yes | No | Yes | No | No | No | Yes | No | No
DENW | Dental Workroom | FFE | MMLA-016 | BURNER: bunsen | 1 |  | Yes | No | No | No | No | No | No | Yes | No
DENW | Dental Workroom | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No