## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DISP-8 | Disposal Room, 8m2 | 8 | 24 Hours |  |  |  | The Disposal Room provides for the temporary holding of clinical waste, general waste, sharps, soiled linen and recyclables prior to removal. The Disposal Room should be located in close proximity to a handwashing basin or be provided within the room (optional) if waste will be handled in this area. The room should be lockable.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DISP-8 | Disposal Room, 8m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | CLTI-008 | CEILING: plasterboard, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | lockable, optional glazed viewing panel to door | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin, if provided | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin, if provided | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | FQCW-017 | BIN: waste, general, 240L | 2 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | HYBA-011 | BASIN: handwash, Type C | 1 | Default = no hand basin: optional with shroud | No | No | Yes | No | Yes | Yes | Yes | No | No
DISP-8 | Disposal Room, 8m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FFE | MMGE-143 | TROLLEY: soiled linen collection | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 | as required | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | Default = no hand basin; to basin, if provided | No | No | No | No | No | No | No | No | No
DISP-8 | Disposal Room, 8m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No