## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DTUR-10 | Dirty Utility, 10m2 | 10 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility provides for cleaning and holding of used equipment for collection and sterilisation elsewhere, disposal of clinical and other wastes and soiled linen, testing and disposing of patient specimens and decontamination and storage of patient utensils such as pans, urinals and bowls.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DTUR-10 | Dirty Utility, 10m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | ELBO-015 | SWITCH: light, single | 1 | two-way | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | ELGP-106 | GPO: single, special, for equipment | 2 | Pan Sanitiser, Utensil Washer, or combined utensil/pan sanitiser optional | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | ELPR-003 | ISOLATOR: electrical, 1ph+n | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | above flushing rim sink | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-029 | HOOK: equipment | 2 | for clean linen bags | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIHR-053 | RACK: pan & urinal | 2 | total of 12 pans/ 12 urinals | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | wet edge | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-146 | CUPBOARD: wall mount, double door, adj shelves, waterproof carcassing | 1 | over bench, optional, for urinalysis equipment | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | @ 350mm AFFL | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYBA-046 | SINK: flushing rim | 1 |  | No | No | Yes | Yes | No | No | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 | hot water | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYTP-006 | HOSE: spray, pressure control | 1 | to flushing rim sink, with flush button | No | No | Yes | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | HYTP-008 | OUTLET: cold water | 1 |  | No | No | Yes | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | SE | HYTP-013 | OUTLET: hot water | 1 |  | No | No | No | Yes | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to sink | No | No | Yes | No | Yes | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 3 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 | not hardwired, combined utensil/pan sanitiser optional | Yes | No | Yes | Yes | No | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FFE | MMIC-097 | WASHER SANITISER: utensil washer | 1 | combined utensil/pan sanitiser optional | Yes | No | Yes | Yes | No | Yes | Yes | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-10 | Dirty Utility, 10m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No