## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
DTUR-S | Dirty Utility - Sub, 8m2 | 8 | 24 Hours | 1 - 2 intermittently |  | Sound attenuation level high, Acoustic privacy is required. | The Dirty Utility - Sub is a small Dirty Utility Room providing for cleaning and holding of used equipment for collection, disposal of clinical and other wastes and soiled linen testing and disposal of patient specimens. Decontamination and storage of patient bedpans, urinals and bowls is optional in the Dirty Utility-Sub. The Dirty Utility -Sub may be located in Allied Health, Imaging or Ambulatory Day Care areas. The room shall not be provided in Inpatient Units used for overnight stay.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
DTUR-S | Dirty Utility - Sub, 8m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | pull handle/push plate, closer | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | ELGP-106 | GPO: single, special, for equipment | 1 | Pan/ Utensil Washer-sanitiser | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to hand basin | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIHR-025 | HOOK: catheter bag | 2 | above rim flushing sink | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIHR-029 | HOOK: equipment | 2 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIHR-038 | RACK: bowl/basin | 1 | optional | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIHR-053 | RACK: pan & urinal | 1 | 6 pans/ 6 urinals, optional | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | wet edge | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIJO-146 | CUPBOARD: wall mount, double door, adj shelves, waterproof carcassing | 2 | for urinalysis equipment | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIJO-158 | CUPBOARD: wall mount, single door, adj shelves, waterproof carcassing | 1 | for urinalysis equipment | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIJO-196 | SHELF: stainless steel, overbench, wall mount | 1 | over bench, optional in lieu of wall mounted cupboards | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | FLVY-004 | FLOOR FINISH: vinyl, seamless, coved, non-slip, safety | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FQCW-004 | BIN: waste, clinical, 120L | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYBA-046 | SINK: flushing rim | 1 | & pressure control hose spray, or slop hopper optional | No | No | Yes | Yes | No | No | Yes | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYBA-052 | SINK: single, 450 x 350 x 250D | 1 |  | No | No | Yes | Yes | Yes | Yes | Yes | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYTP-006 | HOSE: spray, pressure control | 1 | to flushing rim sink, with flush button | No | No | Yes | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | HYTP-008 | OUTLET: cold water | 1 |  | No | No | Yes | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | SE | HYTP-013 | OUTLET: hot water | 1 |  | No | No | No | Yes | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to sink | No | No | Yes | No | Yes | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FFE | MMIC-095 | WASHER SANITISER: pan flusher | 1 |  | Yes | No | Yes | Yes | No | Yes | Yes | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
DTUR-S | Dirty Utility - Sub, 8m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No