## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ECHO | Echocardiography - Trans-oesophageal | 30 | Available 24 Hours | 1 patient; 1 - 2 staff |  | Acoustic privacy is required | Room for diagnostic echocardiography procedures including trans-oesophageal echocardiography. Echocardiography procedures may be performed under local anaesthesia. The Echocardiography room should be located close to patient toilet and change rooms.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ECHO | Echocardiography - Trans-oesophageal | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | DWSC-021 | DOOR: 1400mm c/o, 1 1/2 leaf, solid core, paint | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELBO-015 | SWITCH: light, single | 3 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELGP-101 | GPO: single, ceiling mounted | 1 | exam light | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELGP-106 | GPO: single, special, for equipment | 2 | Echocardigraphy machine, XRV | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELGP-109 | GPO: single, wall mounted | 2 | to exam couch | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ELGP-208 | GPO: double, wall mounted | 4 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIHR-026 | HOOK: coat | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIJO-116 | CUPBOARD: tall, double door, adj shelves | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1 | adjustable shelves | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 2 | over bench | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1 | to entry door | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQBS-014 | CHAIR: client | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQBS-037 | FOOTSTOOL | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | HYBA-010 | BASIN: handwash, Type B | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | 1- bed area; 1 - exam couch; bed and couch may share one point if handset will reach both | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | on services panel and wall mounted | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 2 | 1- bed area; 1 - exam couch; bed and couch may share one point if handset will reach both | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 |  | No | Yes | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | LIFX-008 | LIGHT: task light, built in | 2 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 | optional | Yes | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MGFP-002 | FLOWMETER: medical air | 1 | patient services panel | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | patient services panel | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MMBE-014 | BED: patient, ICU, electric with mattress | 1 |  | Yes | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MMBE-024 | COUCH: examination, manual, mobile | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MMGE-002 | ADAPTER: suction | 1 | patient services panel | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MMGE-152 | VIEWER: X-ray, 2 screen | 1 | optional | Yes | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FFE | MMMI-325 | DEVICE: imaging, echocardiography machine | 1 |  | Yes | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin; tiles also acceptable | No | No | No | No | No | No | No | No | No