## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | 12 | 24 Hours | 1 - 2 staff intermittently |  |  | The Equipment Clean Up Room is used for cleaning of equipment used in patient care or loaned to outpatients following return. Storage will be required for holding cleaning equipment.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | Water resistant flush set suspended also acceptable. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWGL-020 | DOOR: 1100mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Optional. To be decided at project level. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 | Optional | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-008 | DISPENSER: detergent | 1 | To sink. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-018 | DISPENSER: gown | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-022 | DISPENSER: moisturiser | 0 | optional | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIGE-009 | PLATFORM: equipment washing, wall mounted | 1 | Stainless steel, grated, height adjustable, wall mounted. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | Wet edge and inset sink/s. Length to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-117 | CUPBOARD: tall, double door, adj shelves, lockable | 1 | Optional. Number to suit layout. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2 | Over bench. Number to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FIJO-197 | SHELF: stainless steel, underbench | 1 | At 350mm AFFL or underbench, stainless steel cupboard. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1 | Refer to BHWS-B (similar). Elbow action levers or handsfree optional. | No | No | Yes | No | Yes | Yes | Yes | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 1 | hot water | No | No | Yes | Yes | Yes | Yes | Yes | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYDR-004 | DRAIN: floor waste | 1 | To wash bay. | No | No | No | No | No | No | Yes | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-003 | HOSE REEL: retractable | 1 |  | No | No | Yes | No | No | Yes | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-006 | HOSE: spray, pressure control | 1 | Above sink, optional. Depends on operational/infection control policies. | No | No | Yes | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYTP-008 | OUTLET: cold water | 2 | Hose reel and spray hose connection | No | No | Yes | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | SE | HYTP-013 | OUTLET: hot water | 2 | Hose reel and spray hose connection | No | No | No | Yes | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1 | to basin. Elbow action levers or handsfree optional. | No | No | Yes | No | Yes | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FFE | MMGE-119 | TROLLEY: equipment | 1 | Optional. | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
ECL-12 | Equipment Clean-Up/Loan Equipment, 12m2 | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No