## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-ACC | Ensuite - Accessible, 7m2 | 7 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite is for use by a patient with a disability to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The room shall comply with AS1428. The area and layout must accommodate an assisting nurse and a shower commode. Mobile patient lifters will not routinely be used within this space but the ensuite should accommodate this equipment in the case of a patient fall. Additional design requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining floor. The door is to be fitted with escape hardware.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-ACC | Ensuite - Accessible, 7m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 | water resistant set plasterboard ceiling also acceptable | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | optional | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 | locate on drop down rail | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIGE-001 | BENCH SEAT: fixed, fold up/down, wet area, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | drop down rails to sides of WC | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail strength and fixings | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYBA-005 | BASIN: handwash, accessible | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-035 | TAPWARE: mixer, basin, accessible | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FFE | HYWC-001 | TOILET SUITE: accessible | 1 |  | No | No | Yes | No | No | Yes | Yes | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light; may be located on drop down rail beside toilet | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 |  | No | No | No | No | No | No | No | No | No
ENS-ACC | Ensuite - Accessible, 7m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No