## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-BA | Ensuite - Bariatric, 7m2 | 7 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Bariatric is designed to meet the needs of bariatric (obese or morbidly obese) patients allowing the patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The Ensuite - Bariatric is associated with the 1 Bed Room - Bariatric. The area and layout must accommodate two assisting nurses and a shower commode with bariatric capability. The Ensuite and Bedroom will need to be planned as an integral suite so the use of a ceiling mounted hoist is optimised across the two rooms. The choice of Ensuite will depend on the patient type, the Operational Policy and floor layout of the facility. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-BA | Ensuite - Bariatric, 7m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | DWSC-012 | DOOR: 1200mm c/o, 1 1/2 leaf, solid core, paint | 1 | outward opening, privacy latch, emergency release | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 2 | optional | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 2 | optional | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-016 | RAIL: towel | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 2 | 1 near wc/basin, 1 for shower | No | No | No | No | No | No | Yes | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | HYWC-002 | TOILET SUITE: bariatric | 1 |  | No | No | Yes | No | No | Yes | Yes | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | ITCL-031 | PENDANT: nurse call, patient to staff | 1 | waterproof | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | MMBE-061 | LIFTER: patient, ceiling mounted, track, traverse, bariatric | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FFE | MMGE-025 | CHAIR: shower, bariatric | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 | for any areas not covered with vinyl/tile | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No