## RDS
Standard Components - Room Data Sheet
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-BR | Ensuite - Birthing, 7m2 | 7 | 24 Hours | 1 mother; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Birthing Room is for the mother to wash, shower and use the toilet, either independently or with assistance. During labour, the shower, will be used for extended periods to manage pain. The area and layout must accommodate an assisting midwife and a support person. The Ensuite will have direct access from the Birthing Room. The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring.

## Items in room
Standard Components - Items in room
Date of issue: 05.04.2018
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-BR | Ensuite - Birthing, 7m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | DWSC-011 | DOOR: 1100mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIDI-030 | DISPENSER: soap | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 2 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIRT-016 | RAIL: towel | 1 | with grab rail strength and fixings | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | HYDR-004 | DRAIN: floor waste | 2 |  | No | No | No | No | No | No | Yes | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | HYTP-020 | SHOWER: hand-held | 2 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 2 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | HYWC-001 | TOILET SUITE: accessible | 1 | accessible suite assists with mother's mobility | No | No | Yes | No | No | Yes | Yes | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FFE | MMMA-013 | STOOL: birthing | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No