## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | 5 | 24 Hours | 1 patient; 1 staff assisting as required | Sound attenuation level high, Acoustic privacy is required. | The Ensuite - Mental Health will provide a shower, toilet and handbasin for use by patients in a mental health inpatient unit. The Ensuite will be lockable and master keyed from the outside. All fittings and fixtures used in consumer areas of the building must be of a type manufactured and marketed as anti-ligature; and installed in accordance with the manufacturer's instructions. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. Selected fixtures are to have a breaking strain of not more than 15kg (e.g. shower curtain rail). Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 | for High Dependency and intensive care areas, consider plywood or equivalent backing to ceiling finish | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | DWSC-004 | DOOR: 850mm c/o, 180 deg swing, single leaf, solid core, paint | 1 | door swing outward and anti ligature hardware | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ELBO-015 | SWITCH: light, single | 1 | outside door. may optionally be replaced with light motion sensor deactivation switch | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIBM-022 | MIRROR: fixed, safety glass, toughened and laminated, anti ligature | 1 | optional; glued to backing material and screw fixed. some jurisdictions may require material to be polycarbonate | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIDI-038 | DISPENSER: toilet paper, recessed | 1 | recessed or with 15kg breaking strength if wall mounted | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIDI-051 | HOLDER: soap/shampoo, recessed, vertical format | 1 | to shower | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIHR-027 | HOOK: coat, collapsible, anti ligature | 2 | one at 1200AFFL for wheelchair users; dependent on jurisdictional policy | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-004 | GRAB RAIL: shower, anti ligature | 1 | optional, vertical | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-009 | GRAB RAIL: WC, anti ligature | 1 | optional, vertical | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FIRT-029 | TRACK: curtain, plastic, recessed | 1 | optional, for privacy screen to shower area; dependent on jurisdictional policy. 15kg breaking strength recommended | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | FLVY-009 | FLOOR FINISH: vinyl, seamless, coved, wet area, non-slip | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQCW-037 | BIN: waste, sanitary | 1 |  | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | FQGE-011 | CURTAIN: shower | 1 | optional, collapsible; anti ligature fabric; dependent on jurisdictional policy | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYBA-078 | BASIN: with integrated shelf | 1 |  | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | HYDR-010 | DRAIN: floor waste, anti ligature | 2 |  | No | No | No | No | No | No | Yes | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | HYDR-011 | DRAIN: clear out, anti ligature | 1 |  | No | No | No | No | No | No | Yes | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-002 | FLUSH BUTTON: toilet suite | 1 |  | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-019 | SHOWER: fixed rose, anti ligature | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-024 | SPOUT: basin, anti ligature | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-046 | TAPWARE: hot and cold taps, shower, anti ligature | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYTP-047 | TAPWARE: hot and cold taps, basin, anti ligature | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FFE | HYWC-005 | TOILET SUITE: concealed cistern, floor mounted | 1 | accessible height for patient use | No | No | Yes | No | No | Yes | Yes | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | optional, + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | SE | ITSE-045 | SENSOR: motion detection, for lighting control, flush to ceiling | 1 | optional | Yes | Yes | No | No | No | No | No | No | No
ENS-MH-A | Ensuite - Mental Health, Inboard, 5m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | tiles also acceptable | No | No | No | No | No | No | No | No | No