## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-SH | Ensuite - Shared, 6m2 | 6 | 24 Hours | 1 patient; 1 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Shared is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The area and layout must accommodate an assisting nurse, patient lifter and wheelchair access. The Ensuite shared may be accessed from two patient rooms. Special privacy latching will be required to lock both entry doors on activation. The actual choice of Ensuite will depend on the patient type and the Operational Policy of the facility. The Ensuite - Shared may vary in configuration to suit different patient types or room types including: ENS-SH-A Shared ensuite - standard, ENS-SH-B Shared ensuite with additional access. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-SH | Ensuite - Shared, 6m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 2 | outward opening, privacy latch; no. to suit layout of room | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIJO-181 | JOINERY UNIT: vanity, single basin | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 | 1 to side | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | drop down rail, optional for standard shared ensuite | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | to both sides of WC in additional access ensuite | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-016 | RAIL: towel | 2 | with grab rail strength and fixings | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | Tiles also acceptable | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYBA-002 | BASIN: ensuite, with vanity unit | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 2 |  | No | No | No | No | No | No | Yes | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 |  | No | No | Yes | No | No | Yes | Yes | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 2 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FFE | MMGE-024 | CHAIR: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SH | Ensuite - Shared, 6m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No