## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
ENS-SP | Ensuite - Special, 6m2 | 6 | 24 Hours | 1 patient; 1-2 staff assisting |  | Sound attenuation level high, Acoustic privacy is required. | An Ensuite - Super is for a patient to wash, shave, groom themselves, shower and use the toilet, either independently or with assistance. The Ensuite - Super is associated with the 1 Bed Room - Special; the additional area and layout will facilitate two assisting nurses, patient lifter and wheelchair access. The Ensuite - Super may vary in configuration to suit different patient types or room types including: ENS-SP-A Ensuite Super, Inboard, ENS-SP-B Ensuite Super, Stand alone. The actual choice of Ensuite will depend on the patient type, the Operational Policy and floor layout of the facility. Additional Design Requirements: The shower floor must not have a raised hob. The entrance is to be flush with the adjoining flooring. The door is to be fitted with escape hardware.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ENS-SP | Ensuite - Special, 6m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | CLTI-014 | CEILING: plasterboard, water resistant, drop-in tiles, prefinished, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | DWSC-013 | DOOR: 1200mm c/o, single leaf, solid core, paint | 1 | outward opening, privacy latch | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIBM-006 | MIRROR: fixed, glass | 1 | over basin | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-030 | DISPENSER: soap | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-036 | DISPENSER: toilet paper | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIDI-049 | HOLDER: soap/shampoo, non-recessed | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIHR-026 | HOOK: coat | 2 | 1 @ 1200 AFFL for wheelchair users | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-003 | GRAB RAIL: shower, horizontal | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-006 | GRAB RAIL: WC | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-008 | GRAB RAIL: WC, hinged | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-016 | RAIL: towel | 2 | with grab rail strength and fixings | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FIRT-034 | TRACK: curtain, shower, 90 deg | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 | or tiles for a tiled floor | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | FLVY-005 | FLOOR FINISH: vinyl, seamless, coved, non slip, studded | 1 | Tiles also acceptable | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | FQGE-011 | CURTAIN: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | HYBA-012 | BASIN: handwash, Type C, with vanity unit | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-020 | SHOWER: hand-held | 1 |  | No | No | Yes | No | Yes | Yes | Yes | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-036 | TAPWARE: mixer, basin, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | HYTP-039 | TAPWARE: mixer, shower, lever action | 1 |  | No | No | Yes | No | Yes | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | HYWC-006 | TOILET SUITE: patient | 1 |  | No | No | Yes | No | No | Yes | Yes | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 2 | + indicator button & light | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FFE | MMGE-024 | CHAIR: shower | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
ENS-SP | Ensuite - Special, 6m2 | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 | to wet areas; tiles also acceptable | No | No | No | No | No | No | No | No | No