## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
HYDP | Hydrotherapy Pool | 90 | 7am to 8pm, daily | Up to 12 |  |  | Hydrotherapy Pool for patient rehabilitation and exercise under supervision. Pool size 15m x 6 m (not including pool surrounds). Pool and surrounds to comply with AS 3979 - Hydrotherapy Pools. Additional Design Considerations: Depth 0.9 metres to 1.5 metres - gradual slope. Deep end may be reduced if paediatric use is likely to be frequent. Wet deck - single channel. Temperature of water - 33 - 34 degrees. Temperature of air to be no more than 10 degrees below water temperature. Water to be earthed. Pool surface - tiled, non-slip; ensure a high level of slip resistance to tiles on the ramp; vertical surfaces of tiling do not need to be slip resistant. Glazing to pool walls recommended. Ramp access with handrail & stair access with handrails. Pool handrails required - not recessed type. Pool blanket may be required (insulation for energy conservation). Disinfection system to be advised. Pool hydraulic hoist may be required. Underwater pressure jets for therapeutic purposes is optional.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
HYDP | Hydrotherapy Pool | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | CLFS-002 | CEILING: fibre cement, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWGL-001 | DOOR: 910mm c/o, single leaf, fully glazed, alum/safety glass, powdercoat/paint | 1 | alternative Exit if required by BCA; lockable | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWGL-040 | DOOR: 1500mm c/o ,1 1/2 leaf, fully glazed, alum/safety glass, powdercoat/paint | 2 | to Lobby/ Waiting & Exit; lockable, restricted access | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | Observation windows as required | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | to solid core doors | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 5 | to Change Rooms/ Cleaner/ Plant areas; lockable | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | DWWH-005 | WINDOW | 1 | Desirable | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | ELGP-106 | GPO: single, special, for equipment | 1 | motorised pool blanket if required | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | ELGP-112 | GPO: single, wall mounted, waterproof | 4 | waterproof, chlorine resistant | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | FIGE-004 | BENCH SEAT: fixed, indoor, adj lockers | 2 | to concourse, under lockers, optional | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | FIRT-033 | TRACK: curtain, shower | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | FLGE-010 | FLOOR FINISH: tiles, ceramic, non-slip | 1 | Metz' 245x122 or 'Granito' 200x200 are suitable | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | FLSK-004 | SKIRTING: tiles, coved, to match floor tiles | 1 | max 25mmH | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | FQGE-011 | CURTAIN: shower | 2 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | FQSN-050 | LOCKER: 4 tier (quarter size) | 8 | to concourse, on bench seat, optional | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | HYDR-004 | DRAIN: floor waste | 18 | every 3-4 metres on concourse | No | No | No | No | No | No | Yes | No | No
HYDP | Hydrotherapy Pool | SE | HYTP-008 | OUTLET: cold water | 1 | for washing down concourse | No | No | Yes | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | ITBU-009 | CONTROL UNIT: public address system | 1 | announcements, music | Yes | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | ITBU-020 | PUBLIC ADDRESS SYSTEM | 1 | general requirement | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | SE | ITCL-004 | BUTTON: nurse call, emergency | 4 | 1 each side of pool | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | ITCL-016 | CLOCK: clock system slave, analogue | 1 |  | Yes | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | MMAH-017 | HOIST: pool, hydraulic | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FFE | MMAH-032 | BLANKET: pool, auto-operated | 1 | optional | Yes | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 2 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 1 |  | No | No | No | No | No | No | No | No | No
HYDP | Hydrotherapy Pool | FA | WLWA-011 | WALL FINISH: tiles, ceramic, glazed | 1 |  | No | No | No | No | No | No | No | No | No