## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
LAUN-PT | Laundry - Patient, 6m2 | 6 | 24 Hours | 1 - 2 |  |  | Domestic style laundry for patient use. The room will include a bench, laundry tub, domestic style washing machine, dryer and ironing facilities.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
LAUN-PT | Laundry - Patient, 6m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | CLFS-009 | CEILING: plasterboard, water resistant, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | lockable | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | Observation window, optional | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | To be decided at project level. | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | ELGP-111 | GPO: single, wall mounted, RCD protected | 3 | 30mA RCD protection, washer, dryer, ironing cabinet, | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1 | 30mA RCD protection, above bench | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIHR-007 | BRACKET: for dryer | 1 | for dryer | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | With inset laundry tub, open under part. Length to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-135 | CUPBOARD: underbench, double door, adj shelves | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FIJO-143 | CUPBOARD: wall mount, double door, adj shelves | 2 | Over bench. Number to suit layout, refer RLS or project specific requirements. Some lockable space may be needed. | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | FLVY-003 | FLOOR FINISH: vinyl, seamless, coved, non slip | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQCW-056 | MACHINE: washing, domestic | 1 | heavy duty | Yes | No | Yes | Yes | No | Yes | Yes | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQGE-015 | DRYER: clothes, domestic | 1 | wall mounted @ 600mm AFFL on bracket | Yes | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQGE-028 | IRON: clothes, electric | 1 | inside cupboard, hardwired. | Yes | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQSM-030 | TROLLEY: laundry, basket | 1 | under bench | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | FQSN-023 | CABINET: ironing board | 1 | lockable, with integral ironing board | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | HYBA-064 | SINK: single, laundry | 1 | with overflow drain, warm water, sinlge mixer to tub optional | No | No | Yes | Yes | Yes | Yes | Yes | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | HYDR-004 | DRAIN: floor waste | 1 |  | No | No | No | No | No | No | Yes | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | HYTP-008 | OUTLET: cold water | 1 |  | No | No | Yes | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | HYTP-013 | OUTLET: hot water | 1 | to washing machine | No | No | No | Yes | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FFE | HYTP-040 | TAPWARE: mixer, sink, accessible | 1 |  | No | No | Yes | No | Yes | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | SE | MEEX-002 | EXHAUST: dryer | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
LAUN-PT | Laundry - Patient, 6m2 | FA | WLWA-007 | WALL FINISH: splashback | 1 | Selection of material to comply with Part D Infection Prevention and Control AusHFG. | No | No | No | No | No | No | No | No | No