## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MAMMO | Mammography Room | 16 | Available 24 Hours | 1 patient; Up to 2 staff assisting |  | Acoustic privacy is required | X-ray room for mammography imaging. Additional Design Considerations: Radiation shielding as advised by Radiation Consultant. Cable ducts between mammography unit and control area will be required. 'X-ray in Use' lights required outside each entry door.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
MAMMO | Mammography Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
MAMMO | Mammography Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 5
MAMMO | Mammography Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 2 | optional
MAMMO | Mammography Room | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 1
MAMMO | Mammography Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
MAMMO | Mammography Room | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 1 | to basin
MAMMO | Mammography Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | tiled ceiling also acceptable if interventional procedures are not undertaken
MAMMO | Mammography Room | FA | DWSC-005 | DOOR: 910mm c/o, single leaf, solid core, lead shielding, paint | 1
MAMMO | Mammography Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
MAMMO | Mammography Room | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 6
MAMMO | Mammography Room | FFE | FIHR-019 | BRACKET: for suction bottle | 1
MAMMO | Mammography Room | FFE | FIHR-005 | BRACKET: for display screen, PACS, wall mounted | 1
MAMMO | Mammography Room | FFE | FQBS-018 | CHAIR: office, ergonomic | 1 | to desk
MAMMO | Mammography Room | FFE | MMGE-019 | CHAIR: patient | 1
MAMMO | Mammography Room | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
MAMMO | Mammography Room | FFE | FIHR-026 | HOOK: coat | 2 | optional, for patient changing, 1 @1200H
MAMMO | Mammography Room | FFE | FQGE-010 | CURTAIN: privacy screen | 1 | to entry door
MAMMO | Mammography Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1
MAMMO | Mammography Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
MAMMO | Mammography Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
MAMMO | Mammography Room | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 1
MAMMO | Mammography Room | FFE | MGFP-004 | FLOWMETER: oxygen | 1
MAMMO | Mammography Room | FFE | FIHR-055 | RACK: scanhead | 1
MAMMO | Mammography Room | FFE | MMGE-002 | ADAPTER: suction | 1
MAMMO | Mammography Room | FFE | MMGE-100 | SUCTION BOTTLE | 1
MAMMO | Mammography Room | FFE | FQSM-003 | PEDESTAL: mobile, wire basket unit, 840H | 1
MAMMO | Mammography Room | FFE | HYBA-010 | BASIN: handwash, Type B | 1
MAMMO | Mammography Room | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
MAMMO | Mammography Room | FFE | ITCL-014 | CLOCK: analogue, electric | 1
MAMMO | Mammography Room | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | to desk
MAMMO | Mammography Room | FFE | MMMI-159 | DEVICE: imaging, mammography | 1
MAMMO | Mammography Room | FFE | FQDW-028 | WORKSTATION: straight, adj height, 1200W x 750D x 750H nom. | 1
MAMMO | Mammography Room | FFE | MMMI-162 | CONSOLE: control, mammography | 1
MAMMO | Mammography Room | FFE | FIJO-099 | CAC: cable access cap | 1
MAMMO | Mammography Room | FFE | FIRT-040 | TRACK: curtain, privacy, L shaped, angled | 1
MAMMO | Mammography Room | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1
MAMMO | Mammography Room | FFE | FIHR-075 | BRACKET: for computer CPU, underdesk mounted | 1
MAMMO | Mammography Room | FFE | ITNE-068 | COMPUTER: hi performance, for clinical / PACS use, CPU, underbench mount | 1
MAMMO | Mammography Room | FFE | ITNE-070 | DISPLAY SCREEN: PACS | 2
MAMMO | Mammography Room | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 3
MAMMO | Mammography Room | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | to desk, 1 outlet for telephone
MAMMO | Mammography Room | SE | ELPR-006 | RCD: residual current device | 2 | to services panel
MAMMO | Mammography Room | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on service panel
MAMMO | Mammography Room | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 1 | auto on when modality is in use
MAMMO | Mammography Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
MAMMO | Mammography Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
MAMMO | Mammography Room | SE | ITCL-004 | BUTTON: nurse call, emergency | 1
MAMMO | Mammography Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | x-ray viewer
MAMMO | Mammography Room | SE | ELGP-109 | GPO: single, wall mounted | 1 | clock
MAMMO | Mammography Room | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2
MAMMO | Mammography Room | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
MAMMO | Mammography Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | imaging and control equipment
MAMMO | Mammography Room | SE | ITSE-006 | BUTTON: duress, fixed | 1
MAMMO | Mammography Room | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1
MAMMO | Mammography Room | SE | WLSH-004 | SHIELDING: lead lining | 1
MAMMO | Mammography Room | SE | ELBO-012 | SWITCH: light, dimmer | 1
MAMMO | Mammography Room | SE | ELGP-105 | GPO: single, on services panel | 2
MAMMO | Mammography Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2