## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MEET-L-30 | Meeting Room, 30m2 | 30 | Available 24 Hours | Up to 20 |  | Sound attenuation level high, Acoustic privacy is required. | A multipurpose room providing video-conferencing facilities for staff meetings, teaching, training/education and patient group activities. This room may also accommodate other meetings, such as those held with the visiting Magistrate Review Hearings in Mental Health units (refer to AusHFG mental health HPUs for specific requirements), telehealth and for providing video-conferencing facilities for staff and client meetings. The room should be located away from high traffic and noise areas. An external outlook is desirable. A second egress door may be required for staff safety and security. A specific requirement for Magistrate Review Hearings. Integration of video-conference equipment should be considered including but not limited to the following: room and VC control, room sound system, room microphone system (dual, wireless, ceiling or combination), display system (eg, monitor or monitors), AV. Seek audiovisual expertise for complex, project specific requirements. Discussions within the room should not be heard in adjacent rooms or corridor; background noise (from HVAC or other sources) should be kept to a minimum; avoid parallel hard surfaces in the room; acoustic panelling may be considered. Additonal video-conferencing design requirements: Table should be positioned so that all chairs face the camera; tables may be small modular type located together or oval. High level of lighting is required in the room to illuminate faces in view of the camera; avoid bright spots, shadows or dark patches. Room decor should avoid white or pastel colours for optimal picture quality, soft furnishes should avoid busy patterns in camera view. Hard surfaces should be covered to minimise echo. Provide data and ISDN connections and 2 DGPOs for the video-conferencing unit in addition to other power/data provisions in the room; verify locations on site. The room may be located in close proximity to a Beverage Bay and Equipment Bay. Size of space and FF&E quantity/type to be adapted to suit specific project briefing requirements as per AusHFG HPUs. Add 1.2m2 per additional person and allow 1.5m2 for wheelchair parking space as required.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
MEET-L-30 | Meeting Room, 30m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 | Lockable | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWOB-004 | OBSERVATION: internal window, alum/glass, internal blinds, powdercoat | 1 | Optional | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | Optional. To be decided at project level. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | Egress door, may also be required for magistrate's use in Mental Health units, optional. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | DWWD-014 | WINDOW DRESSING: external window, blackout | 1 | Number to align with window configuration, if provided. Window dressing type to comply with Infection Control policy. Blackout required for audiovisual presentations and video-conferencing. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | DWWH-005 | WINDOW | 1 | Desirable. If provided preferably not on a wall in front of the camera. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ELGP-203 | GPO: double, in floorbox | 2 | optional | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ELGP-208 | GPO: double, wall mounted | 7 | 1 above bench, if provided. Verify location of video-conferencing unit before installation. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 2 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 | optional. Length to suit layout, refer RLS or project specific requirements. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 1 | Optional. Number to suit layout, refer RLS or project specific requirements. Storage solution for consumables and equipment to meet project specific Infection Control and OHS requirements. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1 | Slip resistant vinyl also acceptable. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FQBS-017 | CHAIR: meeting room | 20 | May be stackable. Heavy duty for Review Hearings. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FQDW-006 | LECTERN: mobile | 1 | Optional, may incorporate switches, AV computer, power and data. May be more appropriate when two 30m2 meeting rooms are adjacent with an operable wall. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | FQTA-017 | TABLE: rectangular 1200L x 900W, work height | 8 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 1 | Image projection and video-conferencing. Number and size of monitor/s to suit project specific requirements. Interface options to be confirmed at project level. Provide conduit for wiring from monitor/s to services floor box. MATV optional. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light, optional. For patient group/education purposes only. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITIN-022 | OUTLET: data, double RJ45, in floorbox | 1 | optional | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 | On wall for video-conferencing unit (minimum requirement for VC is 1-triple outlet) | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITIN-070 | OUTLET: MATV | 1 | Optional. May be replaced with data outlet, in accordance with ICT policy. May be required for educational purposes, to be determined at project level. If required add television, bracket and dedicated power. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITIN-143 | FLOORBOX: for power, data, AV, flush mounted | 1 | for data and power, optional | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-004 | CAMERA: video conferencing | 1 | Mounted to monitor/s or wall mounted. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-010 | COMPUTER: laptop or other mobile device | 1 | Resident computer or laptop. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-013 | CONTROL UNIT: video conferencing | 1 | Optional, for Mental Health Review Hearings. Console, integral with camera, monitor, speakers and microphone. Configuration and Mental Health Review Board requirement to be confirmed at project level. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-019 | MICROPHONE: videoconferencing | 2 |  | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-042 | SPEAKER: video conferencing, wall mount | 2 | Integral with video-conferencing system. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | ITNE-060 | TELEPHONE: teleconferencing module | 1 | Optional. | Yes | Yes | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | Optional. Refer to HPU requirements. Will not be required in staff-only areas. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FFE | MMOP-060 | RACK: AV | 1 | Optional. May be required for Magistrate Hearings. Integral with video-conferencing system. Requirement to be confirmed at project level. | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | WLWA-001 | WALL FINISH: acoustic panels, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MEET-L-30 | Meeting Room, 30m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 | Decor for video-conferencing to be light/neutral, avoid white and pastel colours, free from patterning, avoid grey/blue-grey shades for optimal picutre quality. | No | No | No | No | No | No | No | No | No