## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
MOR-AU | Mortuary - Autopsy Room | 30 | Available 24 Hours | Up to 4 |  |  | Room for undertaking post mortem examinations. The Autopsy Room should be located adjacent to the Body Cool Store and have ready access to a clean-up area. Additional Design Considerations: Doors to be sealed for odours. Post mortem table to have water flushing system. An observation area is optional.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
MOR-AU | Mortuary - Autopsy Room | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | DWGL-005 | DOOR: 910mm c/o, single leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | DWGL-033 | DOOR: 1400mm c/o, 1 1/2 leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | DWOB-002 | OBSERVATION: internal window, alum/glass, door height, powdercoat | 1 | observation window/s | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | DWPR-006 | DOOR PROTECTION: protection plate, to 900 AFFL, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | equal to Acrovyn | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-105 | GPO: single, on services panel | 2 | to services panel on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-109 | GPO: single, wall mounted | 2 | to bench | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-122 | GPO: emergency power, single, on services panel | 1 | to services panel on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 1 | to bench | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | 900x900, optional | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIHR-016 | BRACKET: for sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIJO-021 | BENCH: 600D, open under, stainless steel lipped | 1 | with wet edge & draining sink | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FIJO-197 | SHELF: stainless steel, underbench | 3 | under SS bench | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-006 | BIN: waste, clinical, 240L | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-016 | BIN: waste, general, 20L | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | FQSM-016 | TROLLEY | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYBA-009 | BASIN: handwash, Type A, scrub | 1 | Refer BHWS-A (similar) | No | No | Yes | No | Yes | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYBA-044 | SINK: draining | 1 | in bench, sensor taps, hot water | No | No | Yes | Yes | No | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYBA-055 | SINK: single, 500 x 450 x 250D | 1 | sensor taps, hot water | No | No | Yes | Yes | Yes | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | SE | HYDR-001 | DRAIN: special requirements | 2 | confirm special requirements at project level | No | No | No | No | No | No | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | SE | HYDR-004 | DRAIN: floor waste | 2 | 1 under sink, with removable filtered trap | No | No | No | No | No | No | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-003 | HOSE REEL: retractable | 1 |  | No | No | Yes | No | No | Yes | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-042 | TAPWARE: sensor | 2 | to sinks | No | No | Yes | No | Yes | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | HYTP-042 | TAPWARE: sensor | 1 | to basin | No | No | Yes | No | Yes | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1 |  | No | Yes | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ITNE-054 | TELEPHONE PABX | 1 | wall phone, handsfree | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | ITSE-029 | INTERCOM: audio, wall mount | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 |  | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to services panel on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | MGAS-073 | OUTLET: tool air, on services panel | 1 | to services panel on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMGE-002 | ADAPTER: suction | 1 | to table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMGE-152 | VIEWER: X-ray, 2 screen | 1 | recessed | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMLA-080 | TABLE: post mortem | 1 | & medical gases to pedestal | Yes | No | Yes | Yes | No | Yes | Yes | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMOP-003 | CABINET: instrument | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMOP-065 | SAW: surgical | 1 |  | Yes | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FFE | MMOP-071 | STOOL: operating, mobile | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | MMSP-025 | SERVICES PANEL: special | 1 | on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | FA | WLWA-020 | WALL FINISH: vinyl, to 1500 AFFL | 1 |  | No | No | No | No | No | No | No | No | No