## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
NBGC | Neonatal Bay - General Care, 5m2 | 5 | 24 Hours | 1 baby; 1-2 staff |  | Sound attenuation level high, Acoustic privacy is required to perimeter walls. | A single bay for the care of well babies away from their mother's bed area which may include treatments such as phototherapy. A staff handwash basin should be provided for each four Neonatal Bays - General Care. An external outlook is required.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
NBGC | Neonatal Bay - General Care, 5m2 | FA | CLCN-006 | CORNICE: plasterboard, 90mm to match ceiling finish, paint | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | DWWH-005 | WINDOW | 1 | Essential | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | ELGP-109 | GPO: single, wall mounted | 2 | shared between 2 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | to serve a group of bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FFE | FQBS-001 | BASSINET | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | optional, shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FFE | MMGE-100 | SUCTION BOTTLE | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | WLPR-019 | WALL PROTECTION: crash rail, at 900 AFFL, prefinished PVC | 1 | Equal to Acrovyn | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No