## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
ORGN | Operating Room - General | 60 | 24 Hours | 1 patient; 5 - 12 staff |  | The Operating Room provides an aseptic environment in which to carry out surgical procedures under local, regional or general anaesthetic. The Operating Room may be used for general surgical procedures that require complex and large equipment. Specialist Operating Rooms can include Neurosurgery, Orthopaedics, Cardiac Surgery, Obstetrics and Trauma. Additional Design Considerations: Minimum critical dimension 7500mm. Laser In Use warning lights may be required outside all exit doors to room if laser equipment is to be used. Lead shielding may be required depending on use of X-ray equipment; to be assessed by Radiation Consultant. External windows are desirable - double glazed with integral venetian blinds. Provide isolated power supply individually to each Operating Room pendant, together with its associated line isolation and overload monitors. Wall gases are required for Obstetric use, for use with a newborn if required. Cardiac Protection, additional power and equipment is required for Cardiothoracic use and some forms of hybrid Operating Rooms. Dimmable LED (or functionally equivalent) lighting is mandatory, the method of dimming is optional.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
ORGN | Operating Room - General | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | DWGL-011 | DOOR: 950mm c/o, single leaf, observation panel, solid core/glass, paint | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | DWGL-051 | DOOR: 1600mm c/o, double leaf, observation panel, solid core/glass, paint | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | DWOB-003 | OBSERVATION: internal window, alum/glass, double glazed, integral venetian blind, powdercoat | 1 | optional, from Store - Sterile Stock | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 6 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | DWPR-011 | DOOR PROTECTION: protection plate, to full height | 5 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | DWWH-007 | SHUTTER: for observation panel, magnetic flap for laser protection | 5 | optional - if laser used | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELBO-003 | CONTROL PANEL: lighting | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELBO-009 | SWITCH: "Laser in use" | 1 | optional, if laser to be used | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELBO-016 | SWITCH: "X-Ray in use" | 1 | optional, if x-ray to be used | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-121 | GPO: emergency power, single, on pendant | 8 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-122 | GPO: emergency power, single, on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2 | for recharging equipment | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-132 | GPO: UPS, single, on pendant | 4 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 3 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELPR-004 | MONITOR: line isolation | 1 | for UPS outlets on pendants | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELPR-006 | RCD: residual current device | 3 | 1 to wall mounted services panel; LIM to be provided to UPS outlets only | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELPR-007 | UPS: status indicator | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ELPR-007 | UPS: status indicator | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIHR-019 | BRACKET: for suction bottle | 2 | optional - for wall mounted gases if provided | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIHR-064 | BRACKET: for display screen, arm mounted, rotating | 2 | attached to MMSP-033 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 | at write up bench | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIJO-013 | BENCH: 450D, open under, stainless steel | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FIJO-100 | BENCH LEGS: stainless steel, for bench top | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | FQSM-039 | TROLLEY: waste bag | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITAV-057 | SPEAKER: ceiling recessed | 2 | supplied with DOR system, optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITAV-060 | CONTROL PANEL: AV integration system, wall mount | 1 | supplied with DOR system | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-005 | BUTTON: nurse call, orderly / porter | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-005 | BUTTON: nurse call, orderly / porter | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITCL-012 | CAMERA: observation | 1 | supplied with DOR system, optional | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITCL-020 | CLOCK: clock system slave, dual digital / elapsed time | 1 |  | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITCL-023 | CONTROL PANEL: master clock system | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 4 | on pendant 1 | No | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITIN-014 | OUTLET: data, single RJ45, on pendant | 4 | on pendant 2 | No | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 |  | No | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITIN-120 | PATCH PANEL: data integration | 2 | supplied with DOR system, one to pendant 1, one to wall | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 2 |  | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITNE-050 | TELEPHONE: handset, desktop, handsfree | 1 | on bench | No | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITNE-052 | TELEPHONE: handset, wall mount | 1 |  | No | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 |  | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 3 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 3 | optional, if x-ray to be used - located outside room entries, delete from list if listed in adjacent rooms - wording on lights subject to jurisdictional legislation | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | LIFX-003 | LIGHT: illuminated sign, "Laser in Use" | 3 | optional, if laser to be used - located outside room entries, delete from list if listed in adjacent rooms | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MEEX-016 | RETURN AIR: grille, low level | 4 | rectilinear or triangular ducts are optional alternatives | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 1 - for complex theatres an additional suction outlet may be required | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 2 - for complex theatres an additional suction outlet may be required | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-074 | OUTLET: tool air, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-074 | OUTLET: tool air, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGFP-001 | ALARM PANEL: medical gases | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MGFP-002 | FLOWMETER: medical air | 4 | 2 for pendants, 2 optional for optional wall outlets | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MGFP-004 | FLOWMETER: oxygen | 6 | 4 for pendants, 2 optional for optional wall outlets | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGFP-007 | CONTROL PANEL: tool air | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-002 | ADAPTER: suction | 8 | 6 for pendants, 2 optional for optional wall outlets | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-014 | CHAIR: anaesthetist | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-045 | IV STAND: mobile | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-048 | LINEN CARRIER: dirty, single | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-078 | PUMP: infusion | 1 |  | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-100 | SUCTION BOTTLE | 2 | optional - for wall mounted gases, if provided | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-122 | TROLLEY: gowns | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-123 | TROLLEY: instrument | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-138 | TROLLEY: preparation | 3 | For setup | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-142 | TROLLEY: sharps bin | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-167 | CHAIR: surgeon | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMGE-168 | STAND: infusion pump, mobile | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-028 | KICKBUCKET & STAND | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-040 | MACHINE: anaesthetic | 1 | recommended to be with integral monitors | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-043 | MACHINE: electrosurgical, diathermy | 1 |  | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-048 | MICROSCOPE: ENT, surgical | 1 | optional - or other specialist surgical equipment | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-069 | STAND: bowl, single | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-071 | STOOL: operating, mobile | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-074 | SYSTEM: smoke evacuation | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-076 | TABLE: mayo | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-080 | TABLE: operating, mobile, electric | 1 | may be supplied with DOR system | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-085 | TROLLEY: anaesthetic | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-096 | DISPLAY SCREEN: AV integration | 1 | supplied with DOR system, wall mounted | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-096 | DISPLAY SCREEN: AV integration | 2 | supplied with DOR system, mounted on operating light arm | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-097 | CAMERA: surgical field, to operating light | 1 | supplied with DOR system, optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-099 | DEVICE: imaging, ultrasound, anaesthetic | 1 | optional | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-100 | WARMER: patient, intraoperative | 1 |  | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMOP-103 | SYSTEM: digital integration in operating rooms (DOR) | 1 | IT and AV system with associated equipment; servers located outside entry to Operating Room | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMSP-033 | LIGHT: operating, 2 arm, light 700 diam nom. / arm for display screen | 2 | supplied with DOR system | Yes | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | FFE | MMSP-034 | PENDANT: single, dual arm, surgical & anaesthetic combined (fixed or adjustable height) | 2 | ergonomic control handles req'd.; shelves optional; nfusion poles optional; pendant services specification assumes mobile plume extraction in use | Yes | Yes | No | No | No | No | No | No | No
ORGN | Operating Room - General | FA | WLWA-019 | WALL FINISH: vinyl, full height | 1 |  | No | No | No | No | No | No | No | No | No