## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-A | Patient Bay, Emergency - Acute Treatment | 12 | 24 Hours | 1 patient; 1-2 staff |  |  | The Patient Bay, Emergency - Acute Treatment may be used for assessment and treatment of patients with acute conditions and will be located within the Emergency Unit. The bay may have partition side nib walls. The Patient Bay will have close access to a staff handwashing basin and, wherever possible, clear line of sight to a staff station.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 | high pressure laminate concealed fixing
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLPR-013 | WALL PROTECTION: corner guards, to 1500 AFFL, prefinished PVC | 3 | as required
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MGFP-002 | FLOWMETER: medical air | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-019 | BRACKET: for suction bottle | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-016 | BRACKET: for sharps bin | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQBS-030 | CHAIR: visitor, patient | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQGE-009 | CURTAIN: bed screen | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-016 | BIN: waste, general, 20L | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIDI-014 | DISPENSER: disposable glove | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQTA-013 | TABLE: overbed | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MGFP-004 | FLOWMETER: oxygen | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | wire basket bins
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-002 | ADAPTER: suction | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-100 | SUCTION BOTTLE | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMBE-011 | BED: patient, emergency, electric | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 | optional, or workstation on wheels
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 | optional
PBTR-A | Patient Bay, Emergency - Acute Treatment | FFE | FIHR-081 | BRACKET: for all-in-one computer, with keyboard shelf, wall mounted, articulated | 1 | optional
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 2 | optional, for cardiac monitor and wall mounted PC, if required
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELPR-006 | RCD: residual current device | 2
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELBO-015 | SWITCH: light, single | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel, + indicator button & light
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | for WOW/ computer
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 | shared between a group of beds
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 3 | optional, for cardiac monitor and wall mounted PC, if required
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MMSP-026 | SERVICES PANEL: wall mounted | 3
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-122 | GPO: emergency power, single, on services panel | 8 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | ELGP-125 | GPO: emergency power, single, ceiling mounted | 1