## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
PBTR-H-9 | Patient Bay - Holding, 9m2 | 9 | 24 Hours | 1 patient; 1 - 2 staff intermittently |  |  | A Patient Bed Bay used for holding of patients prior to procedures, observation of patients following procedures or for assessment and treatment of patients with non acute conditions. The Patient Bay will have close access to a staff handwashing basin. The Patient Bay may be reduced to a minimum of 6m2 to accommodate a recliner chair instead of a patient bed. Requirement for services including medical gases and power will be dependent on the use of the bay.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 | Acoustic tiles acceptable. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ELGP-105 | GPO: single, on services panel | 3 | on services panel, number dependent on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 3 | on services panel, number dependent on use of the bay. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ELGP-208 | GPO: double, wall mounted | 1 | bedhead, Low level, for electric bed and mattress when required. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | Optional. Clinical use. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 | Optional. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1 | required if suction outlet provided | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 | Optional. Depends on functionality, infection control and cleaning policies. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FIRT-025 | TRACK: curtain, bedscreen, U shaped | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | Significant change in colour to be avoided. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FQBS-030 | CHAIR: visitor, patient | 1 | optional | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FQGE-010 | CURTAIN: privacy screen | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FQSN-006 | BIN: storage bins, for wall mounted panel | 3 | on louvred panel, optional | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | FQSN-007 | BIN: storage bins, wire mesh, stainless steel | 1 | For wired panels, optional. Depends on functionality, infection control and cleaning policies. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | LIFX-027 | LIGHT: examination, ceiling mounted | 1 | spatial provision required | Yes | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | LIFX-032 | LIGHT: downlight, examination, ceiling mounted | 1 | optional, or ceiling mounted examination light. Above bed. | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional, required if air outlet provided | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1 | required if oxygen outlet provided | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1 | Or electric recliner chair. Spatial provision for bed may only be required depending on service. | Yes | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | MMGE-002 | ADAPTER: suction | 1 | required if suction outlet provided | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FFE | MMGE-100 | SUCTION BOTTLE | 1 | required if suction outlet provided | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 | flush mounted | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No