## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | 9 | 24 Hours | 1 patient; 1 staff |  | A Patient Bed Bay used for the recovery of patients from anaesthetic, located within the Operating Unit or Day Procedures Unit. A clinical handwashing basin will be provided for each 4 Patient Recovery Bays. Bays will require direct observation from the Staff Station. The use of Workstations on Wheels for reporting should be considered when designing clusters of Stage 1 Patient Recovery Bays.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | DWWD-007 | BLIND: venetian, integral | 1 | optional, required to external window/s if provided | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | DWWH-005 | WINDOW | 1 | optional but desirable | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELBO-015 | SWITCH: light, single | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 7 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ELPR-006 | RCD: residual current device | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-019 | BRACKET: for suction bottle | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-029 | HOOK: equipment | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-033 | PANEL: for storage bins, wall mount | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-067 | BRACKET: for monitor, wall mounted, articulated, adj height | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIHR-068 | BRACKET: for alcohol based hand rub, attached to bed | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIRT-023 | TRACK: curtain, bedscreen, L shaped | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIRT-038 | TRACK: ceiling mounted, IV, straight | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FIRT-043 | RAIL: equipment - horizontal | 1 | provides additional wall protection | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | FQGE-009 | CURTAIN: bed screen | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | on services panel + indicator button & light | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | on services panel, call button on the handset | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 1 |  | No | Yes | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1 | on services panel | No | Yes | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1 |  | Yes | Yes | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 | LED or other lamp of equivalent colour quality | Yes | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MEEX-008 | EXHAUST: low level | 1 | provision is subject to jurisdictional policy | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MGFP-002 | FLOWMETER: medical air | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MGFP-004 | FLOWMETER: oxygen | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMBE-010 | BED: patient, electric with mattress | 1 | optional: to be provided for day patients only. Inpatients will use own bed. | Yes | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-002 | ADAPTER: suction | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-039 | HANGER: IV, for ceiling track | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-100 | SUCTION BOTTLE | 2 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-119 | TROLLEY: equipment | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FFE | MMHA-008 | MONITOR: patient, cardiac with vital signs | 1 | on bracket | Yes | Yes | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | WLPR-001 | WALL PROTECTION: bed protection wall panel | 1 |  | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | WLPR-010 | WALL PROTECTION: corner guards, to 900 AFFL | 2 | optional, for low level duct, if provided | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No