## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
REC-E | Reception, Emergency | 20 | 24 Hours | Up to 3 staff members |  | Sound attenuation required, patient to staff communication acoustic to be considered | A Reception area for the Emergency Unit where patients/ visitors can be received, located adjacent to waiting areas. The room assumes one triage reception point and two administrative reception points, however triage can also be provided as a separate space. One administrative point is DDA compatible and can also be used for accessible triage reception. The number of triage and reception points should be adapted to meet staffing requirements. Additional Design Requirements: security glazing is optional, and subject to jurisdictional requirements; if included consideration of communication and pass-through of samples is required. Several possible door entries are shown: as a minimum a second egress is required for staff. Negative pressure requirement indicates general directional airflow only. Air conditioning to be non recirculating.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
REC-E | Reception, Emergency | FA | FLCP-006 | FLOOR FINISH: carpet, carpet tiles, 90/10 wool/nylon | 1
REC-E | Reception, Emergency | FA | FLSK-009 | SKIRTING: vinyl, feather edged, 150H, prefinished | 11
REC-E | Reception, Emergency | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional
REC-E | Reception, Emergency | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
REC-E | Reception, Emergency | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 2
REC-E | Reception, Emergency | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 2
REC-E | Reception, Emergency | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1
REC-E | Reception, Emergency | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 2 | to waiting area
REC-E | Reception, Emergency | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to triage room
REC-E | Reception, Emergency | FA | DWOB-016 | OBSERVATION: internal window, alum/safety glass, one way, powdercoat | 2 | optional
REC-E | Reception, Emergency | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
REC-E | Reception, Emergency | FFE | FQBS-018 | CHAIR: office, ergonomic | 2
REC-E | Reception, Emergency | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
REC-E | Reception, Emergency | FFE | FQGE-005 | CLOCK: analogue, battery operated | 1
REC-E | Reception, Emergency | FFE | FIJO-131 | CUPBOARD: tall, single door, adj shelves, lockable | 1
REC-E | Reception, Emergency | FFE | FIJO-136 | CUPBOARD: underbench, double door, adj shelves, lockable | 1
REC-E | Reception, Emergency | FFE | FIJO-102 | CUPBOARD: drawer unit | 1
REC-E | Reception, Emergency | FFE | FQCW-016 | BIN: waste, general, 20L | 1
REC-E | Reception, Emergency | FFE | FIHR-006 | BRACKET: for display screen, wall mounted | 4
REC-E | Reception, Emergency | FFE | FQSM-007 | PEDESTAL: mobile, drawer unit, 660H | 3
REC-E | Reception, Emergency | FFE | FIBM-013 | NOTICEBOARD: fixed, fabric covered | 1 | above upstand of benches
REC-E | Reception, Emergency | FFE | FQSN-062 | SAFE: small | 1
REC-E | Reception, Emergency | FFE | MMBE-045 | WHEELCHAIR | 1
REC-E | Reception, Emergency | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1
REC-E | Reception, Emergency | FFE | ITBU-013 | DISPLAY SCREEN: patient flow system | 1
REC-E | Reception, Emergency | FFE | FQGE-037 | MACHINE: cash register | 1
REC-E | Reception, Emergency | FFE | ITNE-007 | COMPUTER: desktop, with display screen | 3
REC-E | Reception, Emergency | FFE | FQGE-038 | MACHINE: electronic funds transfer at point of sale (EFTPOS) | 1
REC-E | Reception, Emergency | FFE | ITSE-048 | DISPLAY SCREEN: CCTV system | 1 | observe amulance bay and other zones as required
REC-E | Reception, Emergency | FFE | FQGE-056 | PRINTER: desktop, labels | 2
REC-E | Reception, Emergency | FFE | ITNE-049 | TELEPHONE: handset, desktop | 3
REC-E | Reception, Emergency | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 3 | behind reception desk, open under part
REC-E | Reception, Emergency | FFE | ITAV-014 | MICROPHONE: surface mounted, gooseneck | 1 | to waiting area speaker
REC-E | Reception, Emergency | FFE | ITNE-021 | MULTIFUNCTION DEVICE: floorstanding | 1
REC-E | Reception, Emergency | FFE | ITAV-051 | DISPLAY SCREEN: audio visual | 3
REC-E | Reception, Emergency | FFE | FIJO-031 | BENCH: 750D, open under, laminate finish | 3
REC-E | Reception, Emergency | FFE | FIJO-185 | JOINERY UNIT: counter top and screen under, emergency reception | 2
REC-E | Reception, Emergency | FFE | FIJO-186 | JOINERY UNIT: counter top and screen under, accessible, emergency reception | 1
REC-E | Reception, Emergency | FFE | WLPT-012 | SCREEN: security, safety glass, with communication slot | 3 | optional, subject to a risk assessment to determine whether required
REC-E | Reception, Emergency | FFE | FIJO-212 | BULKHEAD: joinery | 1
REC-E | Reception, Emergency | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 | for CCTV
REC-E | Reception, Emergency | FFE | FIJO-216 | CUPBOARD: pigeon holes, under bench | 2
REC-E | Reception, Emergency | FFE | FIGE-010 | PASSTHROUGH: to bench | 3
REC-E | Reception, Emergency | FFE | WLPT-014 | SCREEN: acoustic, privacy, safety glass | 4 | optional, subject to a risk assessment to determine whether required
REC-E | Reception, Emergency | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 5
REC-E | Reception, Emergency | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 3 | to workstation bench, 1 outet on each panel for telephone
REC-E | Reception, Emergency | SE | ELBO-015 | SWITCH: light, single | 2
REC-E | Reception, Emergency | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 5
REC-E | Reception, Emergency | SE | ELGP-123.1 | GPO: emergency power, single, wall mounted (V) | 5
REC-E | Reception, Emergency | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
REC-E | Reception, Emergency | SE | ITSE-006 | BUTTON: duress, fixed | 3 | to workstation bench
REC-E | Reception, Emergency | SE | ITSE-038 | READER: access control, general | 2
REC-E | Reception, Emergency | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 3 | to each work station
REC-E | Reception, Emergency | SE | ITSE-028 | INTERCOM: audiovisual, wall mounted | 1 | to ambulance bay and ED entry as required
REC-E | Reception, Emergency | SE | ITIN-029 | OUTLET: data, double RJ45, desk box | 3
REC-E | Reception, Emergency | SE | ELGP-224 | GPO: emergency power, double, desk box | 6
REC-E | Reception, Emergency | SE | ELBO-018 | BUTTON: security, perimeter lockdown | 1 | optional
REC-E | Reception, Emergency | SE | ITIN-145 | DESK BOX: for power, data, AV, flush mounted, softwired | 3