## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
SECL | Seclusion Room | 14 | 24 Hours | 1 patient; 1-2 staff intermittently | Sound attenuation level very high, acoustic privacy is required. | A Seclusion Room provides for the sole confinement of a distressed or agitated person requiring separation for short periods at any hour of the day or night on an involuntary basis. An external outlook is required. All glazing (including external windows) is to be Grade A safety glass to comply with AS/NZS 2208 and AS 1288, specifically, toughened laminated glass with a minimum thickness of 14.28mm, or equivalent approved. Jurisdictional requirements may require an increase in the thickness of the glass for Seclusion Rooms. Door and joinery hardware and any engineering services outlets must not provide ligature points and must be tamper proof. General lighting must be dimmable and/or have controlled switching to create a low stimulus environment. An internal observation window is required so observation is optimised and blind spots eliminated. Designers must carefully consider the design of the door, to ensure it has sufficient strength and robustness but still allows for speech to be heard through it. All finishes to be flush and not provide ligature points. Consider location of wi-fi access points to ensure strong wi-fi coverage is provided for mobile duress functions. Jurisdictional policy to be read in conjunction with guidelines.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
SECL | Seclusion Room | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 | Min. 3000mm height, impact resistant & sealed, robust and not able to be penetrated, consider plywood or equivalent backing to ceiling finish for high dependency and intensive care areas. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWGL-075 | DOOR: 1270mm c/o, single leaf, observation panel, solid core/safety glass, paint | 1 | 50mm solid core door; outward opening, 180 deg swing. Anti ligature hardware; locks to be provided at top bottom and centre of door; key cylinder to centre lock to both sides of door and flush to inside face of door; snibs to top and bottom locks to outside face of door only. Speech to be audible through door, alternatively intercom to be provided. Security-grade noggings will be required to support weight of door and resist attempts to force the door. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWOB-006 | OBSERVATION: internal window, alum/safety glass, double glazed, integral venetian blind, powdercoat | 1 | Grade A safety glass, controls outside room. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | DWWD-007 | BLIND: venetian, integral | 3 | To window, observation panel, controls outside room. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | DWWD-010 | CONTROL: venetian blind, remote | 2 | Outside room, for remote control of blinds to external windows. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | DWWH-005 | WINDOW | 1 | External windows double glazed Grade A safety glass with integral venetians. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | ELBO-015 | SWITCH: light, single | 2 | Outside room, lighting to have controlled switching to create low stimulus environment. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | ELGP-208 | GPO: double, wall mounted | 1 | Outside room, close to entrance door for mechanical emergency equipment. RCD protected as part of patient areas. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | FIBM-004 | MIRROR: fixed, convex, tamper proof, anti ligature | 1 | Securely fixed within a frame and infilled. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | FLSK-011 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished, anti ligature | 1 | Seamless painted bullnose timber capping to match wall function, to terminate/ secure coved vinyl skirting at approx. 40mm off the finished floor level for cleaning purposes, fully glued and screw fixed at 100mm intervals. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | FLVY-002 | FLOOR FINISH: vinyl, seamless, coved, cushioned | 1 | Secure fixings with acoustic underlay. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FFE | FQBS-047 | MATTRESS: foam | 1 | On floor. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | FSDE-004 | DETECTOR: smoke | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | ITSE-006 | BUTTON: duress, fixed | 1 | Optional; outside room. Mobile duress preferred. | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | SE | LIFX-034 | LIGHT: reading light, tamper proof, anti ligature, ceiling recessed | 1 |  | No | No | No | No | No | No | No | No | No
SECL | Seclusion Room | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 1 | Walls to be robust and not able to be penetrated. | No | No | No | No | No | No | No | No | No