## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
STAD | Store - Accountable Drugs | 5 | 24 Hours | 1 - 2 intermittently |  |  | The Store - Accoountable Drugs is a strongroom for storage of accountable (Schedule 8) drugs and medications, located wihin the Pharmacy Unit. Refrigerated storage may also be required. The strongroom will require adequate ventilation and a gate door for security when the main door is open. Accountable drugs storage facilites are to comply with NSW Health Pharmaceuticals Services Branch Policy and the requirements noted in the NSW Police Service document 'Minimising the Risks'. Additional Design Considerations: The strongroom should be independent of the rest of the building structure with no beams or columns passing through the ceiling, walls or floor. The ceiling, walls and floor should be constructed of concrete with a compressive strength of 70 m/p/a with either 1 cm thick tang bar or 1 cm thick reinforcing rods in three levels in a criss cross pattern. The ceiling, walls and floor should be a minimum thickness of 300mm. The door should be torch and drill resistant, fitted with a combination lock facility incorporating duress features and an internal release mechanism in case persons are trapped within. A torch and drill resistant breather tube must be fitted, to comply with Fire Regulations. Security detection equipment should be incorporated into the alarm system, to detect any attack on the structure. A telephone should be installed for staff safety; the telephone should be concealed to restrict unauthorised tampering.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
STAD | Store - Accountable Drugs | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | CLFS-006 | CEILING: plasterboard, flush set, suspended, paint, washable | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | DWGE-002 | DOOR: 910mm c/o, steel, strongroom, grille gate door, paint | 1 | inner door | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | DWGE-003 | DOOR: 910mm c/o, steel, strongroom, security door, paint | 1 | Equal to 'Chubb' Pacific 100 | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ELGP-109 | GPO: single, wall mounted | 1 | refrigerator | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ELGP-208 | GPO: double, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | FIJO-059 | BENCH TOP: 600D, joinery under, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | FIJO-128 | CUPBOARD: tall, shelf unit, pharmacy shelves | 2 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | FIJO-142 | CUPBOARD: underbench, single, adj shelves, with single drawer | 1 | drawer/ cupboard unit | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | FIJO-152 | CUPBOARD: wall mount, shelf unit, adj shelves | 2 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 | 1 outlet for telephone | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | on bench, optional | No | Yes | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ITSE-002 | ALARM: duress | 1 | to entry lock mechanism | Yes | Yes | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | ITSE-004 | ALARM: reed switch | 1 | to door and structure | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | LIFX-008 | LIGHT: task light, built in | 1 | under O/H shelving | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | SE | MEGE-015 | VENTILATION PORT | 1 |  | No | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FFE | MMGE-036 | FRIDGE: drugs, underbench | 1 |  | Yes | No | No | No | No | No | No | No | No
STAD | Store - Accountable Drugs | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No