## Room Data
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Acoustics | Description / Special Requirements
STSS-CC | Store - Sterile Stock, Central Core | 34 | 24 hours | Up to 3 intermittently |  | A room with an aseptic environment for storage and holding of sterile stock for use in the Operating Suite or other acute treatment areas. Sterile stock may be stored in wire mesh shelving either static units, single mobile units or compactus. Structural engineering advice must be sought if compactus is to be used (floor load bearing capacity and potential deflection effect on walls, doors, etc). Top Track compactus may also be used. Size and number/type of shelving to be adapted to suit specific project briefing and WHS requirements as per AusHFG HPUs. Add 1m2 per 900w400d2100h shelving unit. Compactus units as per manufacturer specifications. Storage height to be limited to 520mm min below ceiling to meet Fire Sprinkler system requirements within AS 2118.1. Light fixtures to be sealed.

## Items
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
STSS-CC | Store - Sterile Stock, Central Core | FA | CLCN-008 | CORNICE: square set flush between wall and ceiling, paint | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | CLFS-005 | CEILING: plasterboard, flush set, suspended, paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | DWGL-011 | DOOR: 950mm c/o, single leaf, observation panel, solid core/glass, paint | 2 | auto release, interlock | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 4 | optional | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | DWPR-011 | DOOR PROTECTION: protection plate, to full height | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | ELBO-015 | SWITCH: light, single | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | ELGP-208 | GPO: double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 2 | to benchtop | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FIBM-019 | WHITEBOARD: fixed, magnetic | 1 | optional | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FIHR-065 | BRACKET: for bench, 450D, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FIHR-066 | BRACKET: for display screen, wall mounted, articulated, adj height | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FIJO-013 | BENCH: 450D, open under, stainless steel | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FQBS-052 | STOOL: mobile, high, adj height | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FQSM-015 | SHELVING: stainless steel wire mesh, mobile | 15 | or compactus top-track system, to be determined at project level | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | FQSM-042 | SHELVING: stainless steel wire mesh, for sutures, mobile | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | ITBU-021 | SYSTEM: barcode tracking | 1 | optional, depends on inventory control policy, if required | Yes | Yes | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | ITCL-018 | CLOCK: clock system slave, digital | 1 | mount flush with wall | Yes | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | ITIN-036 | OUTLET: data, triple RJ45, wall mounted | 1 |  | No | Yes | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 | optional, to bench or wall mounted | No | Yes | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | ITNE-066 | COMPUTER: all-in-one, wall mounted | 1 |  | Yes | Yes | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | ITNE-067 | KEYBOARD: keyboard and mouse only | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | LIFX-002 | LIGHT: illuminated sign, "X-Ray in Use" | 2 | wording on light to jurisdictional requirements | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | SE | LIFX-003 | LIGHT: illuminated sign, "Laser in Use" | 2 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FFE | MMGE-138 | TROLLEY: preparation | 3 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | WLWA-005 | WALL FINISH: paint, scrub resistant | 1 |  | No | No | No | No | No | No | No | No | No
STSS-CC | Store - Sterile Stock, Central Core | FA | WLWA-023 | WALL FINISH: vinyl, to 2100 AFFL | 1 |  | No | No | No | No | No | No | No | No | No