## Room Data
Standard Components - Room Data Sheet
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | 13 | 24 Hours | 1 patient; 1 staff, 1 support person |  | Sound attenuation level high, Acoustic privacy is essential. | The Triage Room, Type 2 will provide a private area for initial assessment, physical examination and commencement of first aid of patients presenting to the Emergency Unit. The Triage Room, Type 2 is for Emergency Units that also maintain a separate triage reception function. The room will be located adjacent to, or in close proximity to the triage reception function. Weighing facilities, including baby weighing, should be located nearby. Negative pressure requirement indicates general directional airflow only. Air conditioning to be non recirculating.

## Items
Standard Components - Items in room
Date of issue: 28.05.2019
Generated by dRofus (C) dRofus
Items
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 | floor finish must be minimum slip rating R10; Pendulum P3 or agreed equivalent to extend under basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 6
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWPR-010 | DOOR PROTECTION: to door frame, PVC, prefinished | 1 | optional, to reception door
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLPR-011 | WALL PROTECTION: corner guards, to 900 AFFL min. | 3
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWPR-005 | DOOR PROTECTION: protection plate to 900 AFFL | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 4
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-010 | WALL FINISH: splashback, vinyl | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWOB-007 | OBSERVATION: internal window, alum/safety glass, powdercoat/paint | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWGL-003 | DOOR: 910mm c/o, single leaf, half glazed, solid core/safety glass, paint | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | DWSC-003 | DOOR: 910mm c/o, single leaf, solid core, paint | 1 | optional, to reception
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FA | WLWA-025 | WALL FINISH: vinyl, to 1200 AFFL | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MGFP-002 | FLOWMETER: medical air | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-003 | DISPENSER: bedroll | 1 | or provided as an attachment to exam couch
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-019 | BRACKET: for suction bottle | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-016 | BRACKET: for sharps bin | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQBS-019 | CHAIR: office, ergonomic, high | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQBS-028 | CHAIR: visitor, clinical areas | 1 | consider weight capacity of chair
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-001 | DISPENSER: alcohol based hand rub | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-026 | HOOK: coat | 2 | optional
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIRT-032 | TRACK: curtain, privacy, L shaped | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIRT-031 | TRACK: curtain, privacy | 2 | to internal window as required
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQGE-010 | CURTAIN: privacy screen | 3 | to internal window as required
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-016 | BIN: waste, general, 20L | 1 | 1 to basin, 1 to desk
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-014 | DISPENSER: disposable glove | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-025 | DISPENSER: paper/hand towel | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-030 | DISPENSER: soap | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIDI-031 | DISPENSER: soap antiseptic | 1 | to basin
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FIHR-011 | BRACKET: for monitor, wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MGFP-004 | FLOWMETER: oxygen | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMBE-044 | TROLLEY: patient, transport | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-044 | BIN: waste, sharps, wall mounted | 1 | wall mounted
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-002 | ADAPTER: suction | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-100 | SUCTION BOTTLE | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQSM-016 | TROLLEY | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | FQCW-005 | BIN: waste, clinical, 20L | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | HYBA-010 | BASIN: handwash, Type B | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | HYTP-037 | TAPWARE: mixer, elbow levers | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | ITNE-008 | COMPUTER: for workstation on wheels | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-031 | DIAGNOSTIC SET: wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | LIFX-026 | LIGHT: examination, wall mounted | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMHA-005 | MONITOR: patient, cardiac | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | ITNE-053 | TELEPHONE: handset, wall mount, handsfree | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | FFE | MMGE-164 | WORKSTATION ON WHEELS: clinical, mobile | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITIN-016 | OUTLET: data, single RJ45, wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELPR-006 | RCD: residual current device | 1 | to services panel
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELBO-015 | SWITCH: light, single | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-223 | GPO: emergency power, double, wall mounted | 1 | to WOW
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-006 | BUTTON: duress, fixed | 1 | in discreet location easily accessible by staff
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-038 | READER: access control, general | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITSE-025 | DOOR RELEASE: access control, remote activation | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MMSP-026 | SERVICES PANEL: wall mounted | 2
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ITIN-025 | OUTLET: data, double RJ45, on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-130 | GPO: UPS, single | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | ELGP-122 | GPO: emergency power, single, on services panel | 4