## RDS
Standard Components - Room Data Sheet
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
AusHFG Room Number | Room name | Prog Area | Hours of Operation | Occupancy | Remarks | Acoustics | Description / Special Requirements
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | 9 | 0800 Hours to 1800 Hours, daily | 1 patient, 1 support person, 1 staff assisting |  |  | The Treatment Bay - Renal Dialysis is used for day treatment of patients undergoing renal dialysis treatments. Treatments for each patient may take from 3 to 6 hours, for 3 days per week. Natural light is desirable. Furniture and furnishings should provide a high level of patient comfort and amenity. A staff handwashing basin will be located in close proximity.

## Items in room
Standard Components - Items in room
Date of issue: 20.03.2017
Generated by dRofus (C) dRofus
Items | [6 empty] | Service allocations
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | CLCN-002 | CORNICE: aluminium, 24mm shadow angle, powdercoat | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | CLTI-002 | CEILING: acoustic, drop-in tiles, 600 x 1200 | 1 | Minimum height 2700mm, flush set plasterboard ceiling also acceptable | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | DWWD-006 | BLIND: venetian | 1 | to external windows, if provided | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | DWWH-005 | WINDOW | 1 | Desirable | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELBO-015 | SWITCH: light, single | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELGP-101 | GPO: single, ceiling mounted | 2 | display screen, exam light | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELGP-110 | GPO: single, wall mounted, cleaner | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELGP-123 | GPO: emergency power, single, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELGP-208 | GPO: double, wall mounted | 2 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ELGP-209 | GPO: double, wall mounted, RCD protected | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FIHR-004 | BRACKET: for display screen, ceiling mounted | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FIHR-019 | BRACKET: for suction bottle | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FIRT-023 | TRACK: curtain, bedscreen, L shaped | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | FLSK-010 | SKIRTING: vinyl, floor vinyl coved, 150H, prefinished | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | FLVY-007 | FLOOR FINISH: vinyl, seamless, coved, standard slip resistant | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FQBS-023 | CHAIR: recliner, clinical with attached side table | 1 | or patient bed | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FQBS-030 | CHAIR: visitor, patient | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FQGE-009 | CURTAIN: bed screen | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | FQTA-013 | TABLE: overbed | 1 | may use a fixed table attached to a recliner chair | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | HYDR-006 | DRAIN: tundish | 1 |  | No | No | No | No | No | No | Yes | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | HYTP-015 | OUTLET: reverse osmosis (RO) water | 1 |  | No | No | Yes | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | ITBU-012 | DISPLAY SCREEN: patient entertainment system | 1 |  | Yes | Yes | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITCL-004 | BUTTON: nurse call, emergency | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITCL-006 | BUTTON: nurse call, patient to staff | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITCL-008 | BUTTON: nurse call, staff assist | 1 | + indicator button & light | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITCL-028 | HANDSET: nurse call, with patient to staff call button | 1 | call button on the handset | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITIN-026 | OUTLET: data, double RJ45, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | ITIN-070 | OUTLET: MATV | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | ITNE-049 | TELEPHONE: handset, desktop | 1 |  | No | Yes | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | LIFX-011 | LIGHT: reading light | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | LIFX-013 | LIGHT: procedure, ceiling mounted, small | 1 |  | Yes | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MGFP-002 | FLOWMETER: medical air | 1 | optional | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MGFP-004 | FLOWMETER: oxygen | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MMGE-002 | ADAPTER: suction | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MMGE-049 | MACHINE: dialysis | 1 | if space used for dialysis | Yes | No | Yes | No | No | No | Yes | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MMGE-096 | STATION: dialysis | 1 | if space used for dialysis; RO reticulated water and drain | No | No | Yes | No | Yes | Yes | Yes | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MMGE-100 | SUCTION BOTTLE | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FFE | MMGE-119 | TROLLEY: equipment | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MMSP-026 | SERVICES PANEL: wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | WLPR-002 | WALL PROTECTION: bed protection wall panel, composite, laminate finish | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | FA | WLWA-004 | WALL FINISH: paint, acrylic, washable | 1 |  | No | No | No | No | No | No | No | No | No