## Sheet1
AusHFG Room Code | Room Name | Item list | Item Number | Name | Gross quantity | Comment | Electrical | Data | Cold Water | Hot Water | Warm Water | Tap | Drainage | Gas | Steam
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-BA | 1 Bed Room - Bariatric | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room - Holding, 12m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room - Holding, 12m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-H-12 | 1 Bed Room - Holding, 12m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant
1BR-IC | 1 Bed Room - Intensive Care | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N1 | 1 Bed Room - Isolation - Negative Pressure, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-IS-N2 | 1 Bed Room - Isolation - Negative Pressure, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A1 | 1 Bed Room - Special, Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-A2 | 1 Bed Room - Special, Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-SP-B | 1 Bed Room - CCU, 20m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A1 | 1 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A2 | 1 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-A3 | 1 Bed Room - Inboard Ensuite, Type 3 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B1 | 1 Bed Room - Outboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B2 | 1 Bed Room - Outboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-B3 | 1 Bed Room - Outboard Ensuite, Type 3 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
1BR-ST-D | 1 Bed Room - Back to Back Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A1 | 2 Bed Room - Inboard Ensuite, Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-A2 | 2 Bed Room - Inboard Ensuite, Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
2BR-ST-B | 2 Bed Room - Outboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
4BR-ST | 4 Bed Room - Inboard Ensuite | SE | MGAS-062 | OUTLET: suction, on services panel | 4 | on services panel | No | No | No | No | No | No | No | No | No
ANAE-16 | Anaesthetic Preparation Room, 16m² | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANAE-16 | Anaesthetic Preparation Room, 16m² | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ANAE-16 | Anaesthetic Preparation Room, 16m² | SE | MGAS-062 | OUTLET: suction, on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ANAE-16 | Anaesthetic Preparation Room, 16m² | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANAE-16 | Anaesthetic Preparation Room, 16m² | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ANPR | Angiography Procedure Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on Services Panel 2, to angiography table | No | No | No | No | No | No | No | No | No
ANPR | Angiography Procedure Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on Services Panel 2, to angiography table | No | No | No | No | No | No | No | No | No
ANPR | Angiography Procedure Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on Services Panel 2, to angiography table | No | No | No | No | No | No | No | No | No
ANPR | Angiography Procedure Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on Services Panel 2, to angiography table | No | No | No | No | No | No | No | No | No
ANPR | Angiography Procedure Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on Services Panel 2, to angiography table | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-055 | OUTLET: scavenge, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 2 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-063 | OUTLET: suction, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-023 | OUTLET: medical air (MA), wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-A | Birthing Room - LDR Without Bath | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-063 | OUTLET: suction, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 3 | in cupboard (2), to bath (1) | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-055 | OUTLET: scavenge, wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 2 | in cupboard, to bath | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-023 | OUTLET: medical air (MA), wall mounted | 1 | in cupboard | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
BIRM-B | Birthing Room - LDR With Bath | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | to services panel, infant resuscitaire | No | No | No | No | No | No | No | No | No
CLAB | Catheter Laboratory Procedure Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on Services Panel 2 on table | No | No | No | No | No | No | No | No | No
CLAB | Catheter Laboratory Procedure Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on Services Panel 2 on table | No | No | No | No | No | No | No | No | No
CLAB | Catheter Laboratory Procedure Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on Services Panel 2 on table | No | No | No | No | No | No | No | No | No
CLAB | Catheter Laboratory Procedure Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on Services Panel 2 on table | No | No | No | No | No | No | No | No | No
CLAB | Catheter Laboratory Procedure Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on Services Panel 2 on table | No | No | No | No | No | No | No | No | No
CLUP-P | Clean-Up Room (Pathology), 12m2 | SE | MGAS-023 | OUTLET: medical air (MA), wall mounted | 1 | near sinks for tube cleaning | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS | Consult Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, for paediatric use
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, for paediatric use
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
CONS-ENT-OP | Consult Room - ENT/ Ophthalmology | SE | MGAS-062 | OUTLET: suction, on services panel | 1
CONS-UN | Consult Room - Universal Access | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS-UN | Consult Room - Universal Access | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CONS-UN | Consult Room - Universal Access | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
CTIR | CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
CTIR | CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel
CTIR | CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
CTIR | CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel
CTIR | CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
DENSR-14 | Dental Surgery, 14m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-14 | Dental Surgery, 14m2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-14 | Dental Surgery, 14m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-14 | Dental Surgery, 14m2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENSR-16 | Dental Surgery, 16m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
DENW | Dental Workroom | SE | MGAS-008 | OUTLET: compressed air, wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ECHO | Echocardiography - Trans-oesophageal | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGFP-001 | ALARM PANEL: medical gases | 1 |  | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ENPR | Procedure Room - Endoscopy | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ENS-BA | Ensuite - Bariatric, 7m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 | optional | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | MGAS-033 | OUTLET: nitrous oxide (N2O), wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
ENS-BR | Ensuite - Birthing, 7m2 | SE | MGAS-043 | OUTLET: oxygen (O2), wall mounted | 1 |  | No | No | No | No | No | No | No | No | No
FLUO | Fluoroscopy Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel
FLUO | Fluoroscopy Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel
GENXR | General X-Ray Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel; if located within the ED, quantity of services may need to align with acute treatment bays for trauma use
GENXR | General X-Ray Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel; if located within the ED, quantity of services may need to align with acute treatment bays for trauma use
MAMMO | Mammography Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
MAMMO | Mammography Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1
MOR-AU | Mortuary - Autopsy Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | to services panel on table | No | No | No | No | No | No | No | No | No
MOR-AU | Mortuary - Autopsy Room | SE | MGAS-073 | OUTLET: tool air, on services panel | 1 | to services panel on table | No | No | No | No | No | No | No | No | No
MRICR | MRI Control Room | SE | MEGE-014 | ALARM: oxygen depletion | 1
MRICR | MRI Control Room | SE | MGFP-001 | ALARM PANEL: medical gases | 1
MRIR | MRI Room | SE | MEGE-016 | SENSOR: oxygen depletion | 1
MRIR | MRI Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1
MRIR | MRI Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
MRIR | MRI Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1
MRIR | MRI Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
MRIR | MRI Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBGC | Neonatal Bay - General Care, 5m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | shared between 4 bays | No | No | No | No | No | No | No | No | No
NBICU | Neonatal Bay - Intensive Care, 12m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
NBICU | Neonatal Bay - Intensive Care, 12m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
NBICU | Neonatal Bay - Intensive Care, 12m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 3 | on services panel | No | No | No | No | No | No | No | No | No
NBSC | Neonatal Bay - Special Care, 10m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 |  | No | No | No | No | No | No | No | No | No
NBSC | Neonatal Bay - Special Care, 10m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 |  | No | No | No | No | No | No | No | No | No
NBSC | Neonatal Bay - Special Care, 10m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 1 - for complex theatres an additional suction outlet may be required | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGFP-001 | ALARM PANEL: medical gases | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-074 | OUTLET: tool air, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-074 | OUTLET: tool air, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant 2 - for complex theatres an additional suction outlet may be required | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGFP-007 | CONTROL PANEL: tool air | 1 |  | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-004 | OUTLET: carbon dioxide (CO2), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 2 | optional | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 2 | on pendant 1 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 2 | No | No | No | No | No | No | No | No | No
ORGN | Operating Room - General | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | on pendant 1 | No | No | No | No | No | No | No | No | No
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBAT | Patient Bay, Emergency - Ambulance Triage | SE | MGAS-062 | OUTLET: suction, on services panel | 1
PBIC | Patient Bay - Intensive Care | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 3 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 4 | on tandem pendant
PBIC | Patient Bay - Intensive Care | SE | MGAS-061 | OUTLET: suction, on pendant | 4 | on tandem pendant
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PBTR-A | Patient Bay, Emergency - Acute Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2
PBTR-AS | Patient Room, Emergency - Acute Treatment Special | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-062 | OUTLET: suction, on services panel | 2
PBTR-FT | Patient Bay, Emergency - Fast Track | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
PBTR-H-6 | Patient Bay - Holding, 6m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel, optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-6 | Patient Bay - Holding, 6m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel, optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-6 | Patient Bay - Holding, 6m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel, optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-H-9 | Patient Bay - Holding, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | optional, dependant on use of the bay | No | No | No | No | No | No | No | No | No
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on services panel
PBTR-NA | Patient Bay, Emergency - Non Acute Treatment | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-061 | OUTLET: suction, on pendant | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-041 | OUTLET: oxygen (O2), on pendant | 3 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-031 | OUTLET: nitrous oxide (N2O), on pendant | 1 | optional, on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-021 | OUTLET: medical air (MA), on pendant | 1 | on pendant
PBTR-R | Patient Bay, Emergency - Resuscitation | SE | MGAS-051 | OUTLET: scavenge, on pendant | 1 | optional, on pendant, if N2O provided
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PBTR-RS1 | Patient Bay - Recovery, Stage 1, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PET-CT | PET-CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
PET-CT | PET-CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, on services panel
PLST | Plaster Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
PLST | Plaster Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | Optional. | No | No | No | No | No | No | No | No | No
PLST | Plaster Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
PLST | Plaster Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | If nitrous required. | No | No | No | No | No | No | No | No | No
PLST | Plaster Room | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | on services panel, optional, if N20 required | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
PROC-20 | Procedure Room, 20m2 | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | on services panel, optional | No | No | No | No | No | No | No | No | No
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, on services panel
SPECT-CT | SPECT-CT Imaging Room | SE | MGAS-062 | OUTLET: suction, on services panel | 2 | on services panel
SSTN-10 | Staff Station, 10m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | as required | No | No | No | No | No | No | No | No | No
SSTN-14 | Staff Station, 14m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | as required | No | No | No | No | No | No | No | No | No
SSTN-20 | Staff Station, 20m2 | SE | MGFP-001 | ALARM PANEL: medical gases | 1 | as required | No | No | No | No | No | No | No | No | No
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRIAGE-1 | Triage Assessment Room, Emergency - Type 1 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1
TRIAGE-2 | Triage Assessment Room, Emergency - Type 2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1
TRMT | Treatment Room, 14m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
TRMT | Treatment Room, 14m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 2 | on services panel | No | No | No | No | No | No | No | No | No
TRMT | Treatment Room, 14m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on services panel | No | No | No | No | No | No | No | No | No
TRMT-CHE | Treatment Bay - Chemotherapy, 9m2 | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | on medical gas panel, 1 per 2 bays | No | No | No | No | No | No | No | No | No
TRMT-CHE | Treatment Bay - Chemotherapy, 9m2 | SE | MGAS-062 | OUTLET: suction, on services panel | 1 | on medical gas panel, 1 per 2 bays | No | No | No | No | No | No | No | No | No
TRMT-CHE | Treatment Bay - Chemotherapy, 9m2 | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 | on medical gas panel, 1 per 2 bays | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1 |  | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-022 | OUTLET: medical air (MA), on services panel | 1 | optional | No | No | No | No | No | No | No | No | No
TRMT-RD-A | Treatment Bay - Renal Dialysis Type A | SE | MGAS-062 | OUTLET: suction, on services panel | 1 |  | No | No | No | No | No | No | No | No | No
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-032 | OUTLET: nitrous oxide (N2O), on services panel | 1 | optional, for invasive procedures
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-042 | OUTLET: oxygen (O2), on services panel | 1
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-053 | OUTLET: scavenge, on services panel | 1 | optional, if N2O is required
ULTR-PR | Ultrasound Room - Procedures | SE | MGAS-062 | OUTLET: suction, on services panel | 1